# Protection RCA — User Guide

Audience: Protection engineers, analysts, approvers, and administrators

Product: Protection Disturbance Record (DR) / COMTRADE analysis and Root Cause Analysis (RCA) platform

Document version: 0.9.0

Application: Protection RCA web application (React + FastAPI)

This guide explains how to launch the application (including the portable, no-install build), build the plant hierarchy, bring disturbance records in — either by fetching them directly from the relay over IEC 61850 or by manual upload — analyse each event, interpret the results, generate reports, and complete engineer review. It reflects the current implemented behaviour of the platform.

# Document revision — what is covered in this edition

This edition (0.9.0) expands IEC 61850 acquisition and day-to-day DR review so the product behaves like market tools (Digsi / PCM600 / SCADA COMTRADE pollers): multi-DR fetch, optional COMTRADE path, auto-fetch with settings/SOE, and SOE matched to each DR by time.

| Area | What changed |
| --- | --- |
| Manual Fetch from IED | List records → select one or many DRs → Fetch DR + settings / events. Optional COMTRADE path on IED. Incomplete CFG/DAT pairs are not fetched. See [§10](#10-fetching-records-from-the-relay-iec-61850) |
| Multi-DR | Tick several records (or Select all new); one event per DR. Or skip the list and Fetch — all new complete DRs are taken. See [§10.4](#104-list-and-select-disturbance-records-multi-dr) |
| Auto-fetch + multi-DR | Each poll imports up to 10 new complete DRs (oldest first), one event each, with Settings/Events toggles. Baseline vs import-existing explained. See [§11](#11-automatic-fetch-auto-fetch) |
| SOE / events matched to DR | Large SER/SOE files are time-windowed to each DR (CFG start − 5 s … end + 30 s), or by matching filename to the COMTRADE stem. Settings stay shared. See [§10.7](#107-matching-soe--events-to-the-right-dr) |
| Sequence cards | Engineer-readable facts (element, channel, state 0 → 1, baseline/threshold) instead of raw JSON. Absolute time = CFG start + relative (DR) or SOE wall-clock. See [§17](#17-event-analysis-workspace-detailed) |
| Trips on Summary | Shared trip contacts such as TRIP_CMD (no ANSI in the name) are attributed to the element that picked up before the trip — Summary shows Trips correctly. See FAQ |

Still valid from 0.8.0 (dashboard / upload→Summary / PDF / Users):

| Area | What changed |
| --- | --- |
| Dashboard KPIs | Events with reports counts distinct live events with a report. See [§6](#6-dashboard-operations-console) |
| Upload → Summary | Complete package opens Summary after auto-analyse. See [§9](#9-ied-workspace) |
| Professional PDF | Structured engineering PDF (ReportLab). See [§23](#23-reports-html-pdf-json) |
| Users CRUD | Add / edit / delete local accounts. See [§24](#24-users-sso-and-audit) |

Still valid from 0.7.0 (IEC 61850 & portable) and earlier plant / engineering editions — see previous tables in git history if needed.

# Table of contents

[What this tool is (and is not)](#1-what-this-tool-is-and-is-not)

[Starting and stopping the application](#2-starting-and-stopping-the-application)

[Signing in (local and SSO)](#3-signing-in-local-and-sso)

[Roles and permissions](#4-roles-and-permissions)

[Application layout and navigation](#5-application-layout-and-navigation)

[Dashboard (operations console)](#6-dashboard-operations-console)

[Recommended workflow (end-to-end)](#7-recommended-workflow-end-to-end)

[Plant hierarchy](#8-plant-hierarchy)

[IED workspace](#9-ied-workspace)

[Fetching records from the relay (IEC 61850)](#10-fetching-records-from-the-relay-iec-61850)

[Automatic fetch (auto-fetch)](#11-automatic-fetch-auto-fetch)

[Event numbers](#12-event-numbers)

[All events (list and filters)](#13-all-events-list-and-filters)

[Uploading files manually](#14-uploading-files-manually)

[COMTRADE detection and validation](#15-comtrade-detection-and-validation)

[Running analysis](#16-running-analysis)

[Event analysis workspace (detailed)](#17-event-analysis-workspace-detailed)

[Protection physics and schemes](#18-protection-physics-and-schemes)

[Understanding status badges and quality labels](#19-understanding-status-badges-and-quality-labels)

[Settings and setting hierarchy](#20-settings-and-setting-hierarchy)

[Databases (auth vs plant/events)](#21-databases-auth-vs-plantevents)

[Rules, models, and historical similarity](#22-rules-models-and-historical-similarity)

[Reports (HTML, PDF, JSON)](#23-reports-html-pdf-json)

[Users, SSO, and audit](#24-users-sso-and-audit)

[Supported file types and COMTRADE matrix](#25-supported-file-types-and-comtrade-matrix)

[Sample / test / golden data](#26-sample--test--golden-data)

[Engineering language used in reports](#27-engineering-language-used-in-reports)

[Frequently asked questions](#28-frequently-asked-questions)

[Troubleshooting](#29-troubleshooting)

[Where to find more documentation](#30-where-to-find-more-documentation)

[Quick reference card](#31-quick-reference-card)

# 1. What this tool is (and is not)

## What it is

An engineering decision-support web application that helps you:

Build a plant hierarchy (Substation → Voltage → Bay → Feeder → IED)

Fetch disturbance records, settings and protection events directly from the relay over IEC 61850 (read-only), manually or automatically on a schedule

Upload COMTRADE / ZIP / vendor packages / PDF on each IED when the relay is not reachable

Detect and validate COMTRADE format, revision, container, encoding

Map analog channels and digital DR targets (pickup/trip/52a/…)

Stream and inspect waveforms (raw/scaled samples)

Reconstruct an event timeline from analog/digital channels (+ SOE when available)

Evaluate protection element behaviour and scheme context (including curve/zone physics where inputs exist)

Run a Protection Consistency Check before RCA

Classify faults when electrical evidence is sufficient

Rank RCA hypotheses with supporting / contradicting / missing evidence (+ engineer cause enrichment)

Find historically similar events (supporting only)

Generate controlled HTML / PDF / JSON reports

Record engineer review (accept / modify / reject / inconclusive / field investigation)

## What it is not

| Not this | Why it matters |
| --- | --- |
| Generative AI / ChatGPT / LLM | Conclusions are deterministic rules, calculations, and templates |
| Relay / breaker control | Read-only. IEC 61850 access only *reads* files and data attributes. No control commands, no setting writes, no file deletion on the IED |
| Automatic “relay malfunction” from one inconsistency | Stays INCONSISTENT / INCONCLUSIVE until settings are verified |
| Silent data repair | Malformed COMTRADE is flagged, not quietly fixed |
| Invented fault distance | Shows NOT CALCULABLE when CT/VT/line/settings are missing |

Always ask (the UI is designed around these):

What happened?

Why does the system think that?

Which setting was used?

What evidence supports it?

What evidence contradicts it?

What is uncertain?

What should I verify?

# 2. Starting and stopping the application

## Option A — Double-click launcher (recommended)

Open the project folder protection-rca or the portable folder portable-share

Double-click `ProtectionRCA.exe`

Wait until the browser opens:

Portable mode (when frontend\dist\index.html exists): http://127.0.0.1:8001/

Dev mode (no built UI yet): http://127.0.0.1:5173/

A small window appears: “Protection RCA is running” — it also lists LAN URLs for other PCs

To stop everything: close that window (or click Stop & Close).

This shuts down the API and UI processes started by the launcher.

Keep the control window open while you work. Closing a browser tab alone does **not** stop the services. IEC 61850 auto-fetch also runs only while the application is running.

### What the launcher does on start

Finds a Python runtime — in the portable build it always uses the bundled python\python.exe

Starts the API (FastAPI / uvicorn) on port 8001 and writes its console output to `backend\logs\api-launch.log`

Waits up to 90 seconds for http://127.0.0.1:8001/health to answer (the first launch on a new PC is slower because antivirus scans the files)

Opens the browser and shows the control window

If the API does not come up, the launcher shows “API did not start on port 8001” together with the last lines of `api-launch.log` — that text tells you the real cause (missing file, port busy, database locked, …). See [§29 Troubleshooting](#29-troubleshooting).

## Option B — Share with another person (no install on their PC)

Do not send only the .exe. Build the complete portable folder on your machine, then zip and send it.

cd protection-rca
scripts\build-portable-share.bat

That creates / refreshes protection-rca\portable-share\ containing:

| Item | Purpose |
| --- | --- |
| ProtectionRCA.exe | Launcher |
| python\ | Complete standalone Python runtime with all backend packages (FastAPI, SQLAlchemy, NumPy, ReportLab, IEC 61850 client, …). The other PC needs no Python installation |
| backend\ | API source code, SQLite databases, storage |
| frontend\dist\ | Built web UI — no Node/npm install |
| rules\ | RCA / protection rule catalogs |
| templates\ | Report template and controlled sentence library (needed for HTML/PDF reports) |
| scripts\ | Launcher script used by the exe |
| HOW_TO_RUN.txt | Short start / LAN instructions |

What the build script checks at the end:

portable-share\python\python.exe exists

The bundled Python can import uvicorn, fastapi, sqlalchemy, numpy

If either check fails the build stops with an error instead of producing a folder that will not start on another PC.

The build replaces only backend, frontend, rules, scripts, python and the exe inside portable-share. Any other folders you keep there (for example sample event folders such as 132kV_Feeder_Fault_Events\) are preserved.

On the other laptop:

Unzip the folder anywhere (keep the internal structure — python\, backend\, frontend\ must stay next to the exe).

Double-click ProtectionRCA.exe.

Browser opens http://127.0.0.1:8001/.

Close the control window to stop.

Requirements: Windows 10/11 64-bit. Nothing else. Antivirus may scan the first launch — allow the app if prompted.

Always rebuild `portable-share` (and re-zip it) after updating the application, otherwise colleagues keep running the old version.

## Option C — Network access while you run it (LAN)

Use this when your laptop hosts the app and colleagues open it from their browsers on the same Wi-Fi / office LAN.

Start ProtectionRCA.exe on the host laptop (portable mode preferred).

Read the LAN URL in the control window, for example: http://192.168.1.50:8001/

When Windows Firewall asks, allow access on private networks (port 8001, or 5173 in pure Vite/dev mode).

Colleagues open that LAN URL in Chrome or Edge.

Important:

Other PCs must not use http://127.0.0.1:... — that only works on the host.

Use a trusted LAN only (not the public internet).

Event data stays on the host PC:

Plant + events: backend\protection_rca_local.db

Users / passwords: backend\protection_rca_auth.db

For IEC 61850 fetch, it is the host PC (the one running the exe) that connects to the relays, so the host must be able to reach the relay network on TCP port 102.

## Option D — Scripts (developers)

cd protection-rca
scripts\start-all.bat

Or separately:

scripts\start-backend.bat
scripts\start-frontend.bat

To force Vite/dev UI even when frontend\dist exists:

set PROTECTION_RCA_DEV=1
ProtectionRCA.exe

Launcher environment variables:

| Variable | Default | Purpose |
| --- | --- | --- |
| PROTECTION_RCA_PORT | 8001 | API (and portable UI) port |
| PROTECTION_RCA_HOST | 0.0.0.0 | API bind address (all interfaces → LAN access) |
| PROTECTION_RCA_UI_PORT | 5173 | Vite dev UI port |
| PROTECTION_RCA_DEV | — | 1 forces dev (Vite) UI |
| PROTECTION_RCA_PORTABLE | — | 1 forces portable mode |

| Service | Typical URL |
| --- | --- |
| Web UI (portable) | http://127.0.0.1:8001 |
| Web UI (dev / Vite) | http://127.0.0.1:5173 |
| API docs | http://127.0.0.1:8001/docs |
| Health | http://127.0.0.1:8001/health |
| LAN (others) | http://<your-PC-IP>:8001/ (portable) |

## Option E — Docker Compose (full stack)

cd protection-rca
docker compose up --build

Services typically include: frontend, backend, PostgreSQL, Redis/Celery worker, MinIO object storage.

Database migrations: Alembic revision 0001_initial_schema creates the application schema. Local scripted / portable runs use two SQLite files (see [§21](#21-databases-auth-vs-plantevents)); Compose uses PostgreSQL for application data.

See README.md and docs/DEPLOYMENT.md.

## Folder layout reminder

ProtectionRCA.exe must stay inside the protection-rca folder or the portable-share folder so it can find:

python\ (portable) or backend\.venv (developer machine)

backend\

frontend\ (portable needs frontend\dist\; dev may also use Node via .tools\node\ or a system install)

rules\ (analysis catalogs)

Rebuild the launcher after launcher script changes:

scripts\build-launcher-exe.bat

# 3. Signing in (local and SSO)

## Local username / password

Open the UI.

Enter Username and Password.

Click Sign in.

Default bootstrap account (empty auth database / first launch):

| Field | Value |
| --- | --- |
| Username | admin |
| Password | admin123 |

Change this password in production. There are no demo events or demo plant assets by default.

## Optional SSO (OIDC)

If the server is configured with AUTH_MODE=oidc and a valid issuer / client:

The login page shows Sign in with SSO (OIDC)

API exposes GET /api/auth/mode and POST /api/auth/oidc/callback

First-time OIDC users are provisioned as VIEWER until an admin elevates the role

If OIDC is not configured, only local login is shown.

## First-time admin (custom bootstrap)

Override defaults before first launch:

set BOOTSTRAP_ADMIN_USERNAME=admin
set BOOTSTRAP_ADMIN_PASSWORD=your-strong-password
set BOOTSTRAP_ADMIN_EMAIL=admin@example.com

Then launch the backend/exe again. This creates only an admin user in the auth database — no sample substations or events.

## Sign out

Click the sign-out icon (arrow out of a door) at the right end of the top bar.

# 4. Roles and permissions

| Role | Typical use |
| --- | --- |
| VIEWER | Read dashboards, events, reports, IEC 61850 connection status |
| ANALYST | Build plant, upload on IED, test / browse / fetch from IED, switch auto-fetch on/off, Check now, start analysis, delete events |
| PROTECTION_ENGINEER | Settings, consistency interpretation, review actions |
| APPROVER | Approvals, audit access |
| ADMIN | Users, rules/models administration |

Higher roles include the rights of lower ones. Authorization is enforced on the server. If a button fails with “forbidden”, your role is insufficient.

# 5. Application layout and navigation

## Sidebar (left)

| Group | Menu | Purpose |
| --- | --- | --- |
| — | Plant | Build and browse the hierarchy; open an IED to fetch or upload records |
| Analysis | Dashboard | Work inbox, KPIs, trend, attention queue, recent events |
| Analysis | All events | Global list with search + date filters; Compare; Continue last event |
| Administration | Users | Account administration |
| Administration | Audit | Audit trail |
| Footer | Help & guide | In-app help and this user guide |

Collapse / expand: the chevron button at the bottom of the sidebar shrinks it to an icon rail (hover an icon to see its name). The choice is remembered in your browser.

**Removed from the sidebar (by design):** standalone **Create event** and **Upload** pages. Records always come in through **Plant → IED** (fetch or upload). Old `/events/new` and upload-only routes redirect to **Plant**.

## Top bar

| Element | Purpose |
| --- | --- |
| Breadcrumb | Protection RCA › <page> (Plant hierarchy, IED workspace, Dashboard, All events, Event analysis, Compare events, Users, Audit trail, Help & guide) |
| COMTRADE RCA chip | Environment indicator |
| Theme icon | Switch light / dark theme (remembered per browser) |
| User chip | Your initials, name and role |
| Sign-out icon | Log out |

## Common UI conventions

Pills / badges are colour-coded by meaning (green = good/complete, amber = warning/review, red = failed/high, grey = not available). Hover a badge for its full glossary text.

Primary (filled) buttons perform the main action of a section; outline buttons are secondary.

Destructive actions (delete) always ask for confirmation.

Tables scroll horizontally on narrow screens; the page itself stays full width.

# 6. Dashboard (operations console)

The dashboard is the engineering operations console. It uses live database values — never fabricated demo events. Layout is full width of the main content area. Returning to the Dashboard (or focusing the browser tab) refetches the KPIs so counts stay aligned after you create or delete events elsewhere.

## Work inbox

Top banner summarises items needing attention (analyse · review · consistency · high severity) with quick buttons:

Review queue

Consistency

Analyse

Recent chips show short, informative labels (event number, feeder / plant context, status) for locally opened events. Continue \<event id\> jumps back into the last worked event (stored in browser memory; pruned when that event is deleted or the events DB is empty).

Header actions: Continue · Compare · All events · Open Plant.

## Clickable KPI tiles (two groups)

Each tile opens All events with the matching filter (?queue=…):

Operations

| KPI | Filter meaning |
| --- | --- |
| Total events | All recorded disturbances |
| Awaiting analysis | Uploaded / queued / analysing |
| Awaiting review | Engineer disposition needed |
| Events with reports | Distinct events that still exist and have a ready report (HTML / PDF / JSON). Not a count of every regenerated file. Increases when a report is generated for an event; decreases when that event is deleted |

Quality & findings

These tiles are problem counters. A value of 0 is good — the tile shows a clear zero-state label instead of looking like “missing data”:

| KPI | When &gt; 0 | When 0 (healthy) |
| --- | --- | --- |
| Protection consistency | Events with INCONSISTENT findings | Clear |
| High / critical findings | HIGH / CRITICAL consistency findings | None |
| RCA inconclusive | Decision INCONCLUSIVE / DATA_INSUFFICIENT | None |
| Parser / DQ issues | WARNING / POOR / INVALID data quality | Good |

Tiles re-flow automatically to the screen width. Click any tile to open the matching event queue.

## Event trend (7 / 30 / 90 days)

Stacked bars for Analysed · Review · Issues. Switch the window with 7d / 30d / 90d. Sparse periods zoom to active days so bars stay readable; values and a peak marker help you spot busy days quickly.

## Attention required + Data quality

Right-hand stack:

Attention required — prioritised events (awaiting review/analysis, DQ, high severity, inconclusive). Each row links into the event workspace.

Data quality overview — donut from real data_quality counts (GOOD / ACCEPTABLE / WARNING / POOR / INVALID / …).

## Recent events table

Columns:

Event ID · Date/Time · Substation/Bay · Relay · Fault · Protection (e.g. 51N, 87T) · Consistency · RCA · Status · Severity · DQ

Events created by IEC 61850 fetch or auto-fetch appear here exactly like uploaded events.

## Empty database behaviour

When there are zero events:

All counters show 0 (Quality tiles show Clear / None / Good)

Banner: “No disturbance events yet”

Action: Open Plant

Checklist: Build Plant (SS → kV → Bay → Feeder → IED) → Fetch or upload on IED → Validate → Analyse → Consistency → RCA → Report

No fake demo events are seeded unless you explicitly enable a demo mode (not default).

# 7. Recommended workflow (end-to-end)

1.  Open Plant                          (/plant)
2.  Create Substation
3.  Add Voltage level (e.g. 132kV)
4.  Add Bay (e.g. Bay 1 / line1 bay)
5.  Add Feeder
6.  Add IED (relay)                     → Open IED
7.  Bring the record in:
      a) Fetch from IED  → IP + vendor → Test connection → Browse IED
                         → tick record(s) → Fetch & create event
      b) or switch on Auto-fetch new records (server does it on schedule)
      c) or Manual upload → drop CFG+DAT / CFF / ZIP / vendor package
8.  Confirm COMTRADE detection / validation (Overview Inputs chips help)
9.  Setup → Channel map + DR targets (correct if auto-infer looks wrong)
10. Start / Re-run analysis (background — watch the status lamps)
      (complete upload / fetch with COMTRADE + settings starts automatically
       and lands on Summary)
11. Read the one-page Summary, then Inspect DR workspace / Waveforms / Sequence
12. Review Electrical + Fault + Location + Protection
13. Study Consistency (setting source!)
14. Study RCA + Evidence (+ cause enrichment if field evidence exists)
15. Download Report (HTML / PDF)
16. Complete Engineer Review

Do not skip Consistency when RCA looks “confident.” Consistency findings often explain why RCA must stay inconclusive.

After changing Channel map, DR targets, settings, or cause evidence, always Re-run analysis so timeline, protection, consistency, and RCA refresh.

Use All events for a global view and filters; use Plant → IED to bring in records for the correct relay.

# 8. Plant hierarchy

Open Plant in the sidebar (route /plant, breadcrumb “Plant hierarchy”).

## Hierarchy levels

Substation
  └── Voltage level (e.g. 132kV)
        └── Bay (e.g. Bay 1)
              └── Feeder
                    └── IED (relay)  ← fetch / upload + events live here

## Level stat cards

Five numbered cards at the top — 1 Substations · 2 Voltage levels · 3 Bays · 4 Feeders · 5 IEDs — show how many of each exist and remind you of the build order. Each level has its own colour and icon, used again in the tree.

## Adding items

| Level | How to create | Notes |
| --- | --- | --- |
| Substation | + Substation (page header) | Top of the tree |
| Voltage | On a substation row → + Voltage | Enter the name and optional kV |
| Bay | On a voltage row → + Bay | Name the bay clearly (e.g. line1 bay) |
| Feeder | On a bay row → + Feeder |  |
| IED | On a feeder row → + IED | Relay / IED name; becomes the fetch/upload target |

Clicking any + button opens the add bar above the tree: “New bay under *132kV*”. Type the name and press Enter or Save; press Esc or Cancel to close. The parent row is expanded automatically so you see the new item.

## Working with the tree

| Control | Purpose |
| --- | --- |
| Twisty / row click | Expand or collapse a level |
| Filter by name or tag | Shows only matching items (and their parents); expand/collapse buttons are disabled while filtering |
| Expand all / Collapse all | Open or close the whole tree |
| Open (IED row) | Go to the IED workspace |
| Event count (IED row) | Number of events attached to that relay |
| Delete (trash icon) | Removes the item and all children — confirm carefully |

The section header shows “*N IEDs · M events · open an IED to fetch or upload records*”.

When the plant is empty you see No plant yet with an Add first substation button.

## Naming tips

Use site names operators recognise (Substation 2, 132kV, Bay 1, Feeder 1, IED-4)

Prefer verified relay tags — the tag is used in fetched file names (e.g. iec61850_settings_<tag>.json)

Never invent plant topology that does not exist on site

# 9. IED workspace

On an IED row click Open. The breadcrumb shows IED workspace.

## Header

Plant path: Substation › Voltage › Bay › Feeder

IED name as the title

Chips: relay Tag, kV (from the voltage level), IP (once an IEC 61850 connection has been saved)

Stats: Events (total for this relay) · In review · Last event (how long ago the newest event occurred)

## Acquire panel — two modes

A segmented switch at the top of the panel selects how records come in:

| Mode | Use when |
| --- | --- |
| Fetch from IED | The relay is reachable over the network (IEC 61850 / MMS). See [§10](#10-fetching-records-from-the-relay-iec-61850) and [§11](#11-automatic-fetch-auto-fetch) |
| Manual upload | You have files exported from the relay tool, e-mail, USB, etc. See [§14](#14-uploading-files-manually) |

Manual upload shows a drag-and-drop zone. Dropped or picked files appear as file chips (name + size, with × to remove) before you confirm; Clear N files empties the list.

| Package | Button label | What happens |
| --- | --- | --- |
| COMTRADE and settings present | Upload, analyse & open summary | Creates the event, starts analysis, opens the Summary tab |
| Incomplete (e.g. CFG without DAT, or no settings) | Upload & create event | Creates the event only; a note asks for CFG + DAT (or CFF) and a settings file for automatic analysis |

After a complete upload you land on Summary — the one-page disturbance story — not the Files tab. Use Files later if you need hashes or to add more attachments.

## Events for this IED

Below the acquire panel, a list of all events attached to this relay (newest first) with event number, date/time, fault/protection, status and DQ badges. Click a row to open the event workspace.

Events are always created with a relay_id (IED). There is no “orphan” upload path in the current UI.

# 10. Fetching records from the relay (IEC 61850)

The Fetch from IED mode pulls disturbance records straight from the relay using the IEC 61850 MMS protocol — the same class of workflow as Digsi, PCM600, AcSELerator, and SCADA COMTRADE pollers (GeoSCADA, WinCC OA, Elipse, ABB 800xA).

It is read-only: the platform only reads directory listings, files and data attributes. It never operates controls, never writes settings and never deletes files on the IED.

## 10.1 Prerequisites

| Requirement | Details |
| --- | --- |
| Network path | The PC running the application must reach the relay IP on TCP port 102 (MMS). Check firewalls / VLAN routing between the engineering PC and the station bus |
| MMS file services | The relay must allow file transfer over MMS (e.g. ABB PCM600: *Communication → IEC 61850 → MMS file transfer*). Without it, settings/status can still be read but records cannot be listed |
| Free client connection | Relays accept a limited number of MMS clients; the SCADA/gateway may already use some |
| Client library | The backend package pyiec61850-ng (libiec61850). It is included in requirements.txt and in the portable build. If it is missing, the panel shows a warning and the server answers 503 |
| Role | ANALYST or higher |

## 10.2 Relay connection

| Field | Default | Notes |
| --- | --- | --- |
| IP address | (empty) | Relay station-bus IP (or host name) |
| Port | 102 | Standard MMS port |
| Vendor | Auto-detect | Hints which folders to search first (see [§10.3](#103-vendor-profiles)) |
| COMTRADE path on IED (optional) | (empty) | Same idea as ABB 800xA / Elipse “remote COMTRADE directory”. Leave blank to auto-walk /COMTRADE/ and the file store. Paste a path from the relay tool or manual when Browse finds nothing |

After any successful test, browse or fetch, the IP, port, vendor and COMTRADE path are saved on the IED and pre-filled next time. The IP also appears as a chip in the IED header.

Click Test connection. On success the panel shows nameplate, detected profile, logical-device count, whether file services are available, and round-trip time.

Nameplate is read from LPHD.PhyNam / LLN0.NamPlt

file services NOT available means records cannot be listed or downloaded (settings/status can still be read)

Connect timeout 10 s, per-request timeout 20 s

**Where do COMTRADE paths come from?** Not from the internet. Market tools either **browse the IED** or let you set the path from the vendor configuration tool / IED manual. This product does the same.

## 10.3 Vendor profiles

| Profile | Families (examples) | Where records are looked for |
| --- | --- | --- |
| Auto-detect | Any IEC 61850 Ed1 / Ed2 / Ed2.1 with MMS file services | /COMTRADE/ then vendor folders once nameplate is known |
| ABB / Hitachi Energy | Relion 605…670 series | /COMTRADE/, /DR/, … ; events /EVENTS/ |
| Siemens | SIPROTEC 5 / 4 EN100, Reyrolle 7SR5 | /COMTRADE/<LD>/, /FAULTREC/, /REC/ |
| GE Vernova (Multilin) | UR / UR+, 8 Series | /COMTRADE/, /OSCILLOGRAPHY/, root OSC*.CFG |
| Schneider Electric | MiCOM / Easergy / Sepam | /COMTRADE/, /DR/, /DISTURBANCE/ |
| Schweitzer (SEL) | 4xx / 7xx / RTAC | /COMTRADE/, /EVENTS/; settings /SETTINGS/ |
| NR Electric | PCS-9xx | /COMTRADE/, /RECORD/, /WAVE/ |
| Toshiba / ZIV / Other | GR / ZLV / generic | /COMTRADE/ plus vendor-specific folders |

Auto-detect is enough for most relays. If Browse is empty, set COMTRADE path (e.g. /COMTRADE/) or pick the vendor explicitly.

## 10.4 List and select disturbance records (multi-DR)

Click List records on IED (later Refresh list).

The table lists every COMTRADE-style record found:

| Column | Meaning |
| --- | --- |
| (checkbox) | Select the record(s) to fetch |
| Record | Base name + directory on the IED |
| Recorded | File-store time |
| Files | Members (CFG, DAT, HDR, INF, CFF, …) |
| Size | Total size |
| Status | Complete · Incomplete · Already fetched (link to the existing event) |

All new complete records are pre-selected. Use Select all new / Clear, or tick individually.

Click Fetch DR + settings / events.

Multiple DRs → multiple events: each selected complete record becomes its own event (EVT-YYYY-NNNNN), with that record’s COMTRADE files. Settings/SOE ride along (see [§10.7](#107-matching-soe--events-to-the-right-dr)).

Shortcut: you can click Fetch without listing first — the app lists the IED and takes all new complete DRs.

Browsing is limited to about 90 s. After a successful list, Found under: shows directories where records were discovered (click to set as COMTRADE path).

## 10.5 Fetch options (with every DR)

| Option | Default | What it does |
| --- | --- | --- |
| Also fetch settings | On | Settings files from the store and SP/SG/CF reads on protection LNs → iec61850_settings_<tag>.json |
| Also fetch events / SOE | On | Event/log files and start/trip/breaker status → iec61850_soe_<tag>.csv (then matched to each DR) |
| Also fetch SCL (CID/ICD) | Off | SCL as attachment only (manual fetch; not in auto-fetch) |
| Description | — | Optional text stored on the created event(s) |

The primary button is always Fetch DR + settings / events (wording adjusts with how many DRs are selected). Disturbance records are always included when complete ones exist — this is not a settings-only path when DRs are available.

Acquisition time budget ≈ 240 s. Warnings appear under “*N warning(s) during fetch*”; the event still holds whatever was retrieved.

## 10.6 What gets created per DR

| File on the event | Content |
| --- | --- |
| *.cfg / *.dat / *.hdr / *.inf / *.cff / *.cev | Immutable COMTRADE members (SHA-256) |
| iec61850_settings_<tag>.json | Mapped settings + iec61850_raw |
| iec61850_soe_<tag>.csv | SOE rows for this DR’s time window (or full snapshot if untimed) |
| Vendor settings / event files | When present and matched |
| SCL | If SCL option ticked |

Settings are read from protection P\* / related R\* LNs, TCTR / TVTR / XCBR, FCs SP / SG / CF, active group LLN0.SGCB.ActSG.

DR time on the event prefers the COMTRADE trigger/start from the CFG; otherwise the file-store “Recorded” time. Acquisition metadata (method IEC61850_MMS, MANUAL/AUTO, host, record key, nameplate) is stored on the event. Audit: `IEC61850_FETCH`.

## 10.7 Matching SOE / events to the right DR

When the IED has a large sequential-event (SER) history, the platform must not attach every row to every disturbance.

| Priority | Rule |
| --- | --- |
| 1. DR digitals | COMTRADE pickup / trip / 52a on that record = primary evidence |
| 2. Filename | Event/SOE file name contains the COMTRADE record stem → that DR only |
| 3. Time window | Keep SOE CSV rows in DR start − 5 s … DR end + 30 s (CFG start + record duration) |
| 4. Settings / SCL | Shared to every DR package (not time-sliced) |

During analysis the Sequence tab merges SOE into the timeline using the same window, so Summary / Sequence stay focused on this fault.

## 10.8 After the fetch

One event created → often opens Summary (or Files, depending on package readiness / UI path).

Several events → IED event list refreshes.

Package ready (COMTRADE and settings) → analysis can start automatically.

Browse again → those records show Already fetched (no accidental duplicates).

## 10.9 Good practice

Test connection first (correct relay / nameplate).

Keep Settings and Events on for consistency and Sequence enrichment.

Map Channel map and DR targets once per new relay type.

Incomplete record → wait and Refresh list (relay may still be writing).

Empty Browse → enable MMS file transfer; set COMTRADE path; pick vendor.

# 11. Automatic fetch (auto-fetch)

The Automatic fetch card lets the server watch the relay and import every new disturbance record without the browser staying open — like SCADA COMTRADE polling.

## 11.1 Switching it on

Enter IP (and vendor / COMTRADE path) and preferably Test connection.

Set options (below) — options lock while auto-fetch is on.

Turn on Auto-fetch new records and choose the interval (1 min … 4 h).

Cannot enable without an IP. Settings save immediately on the IED.

## 11.2 Options

| Option | Default | Meaning |
| --- | --- | --- |
| Settings | On | Download / read settings with every new DR |
| Events | On | Download / read SOE / protection status with every new DR (then matched per [§10.7](#107-matching-soe--events-to-the-right-dr)) |
| Start analysis automatically | On | Queue analysis when COMTRADE + settings are present |
| Also import records already on the IED | Off | Editable only while auto-fetch is off. First cycle also imports the backlog (still max 10 per cycle) |

SCL is not fetched by auto-fetch (use manual Fetch if needed).

## 11.3 Multi-DR behaviour each poll

List complete COMTRADE records on the IED.

Skip already-fetched keys (and the first-run baseline, unless import-existing is on).

Sort remaining by oldest first.

Import up to 10 new DRs this cycle.

One event per DR, with settings/SOE according to the toggles.

Optionally start analysis on each package-ready event.

Any leftover new DRs wait for the next interval.

| Situation | What happens |
| --- | --- |
| First enable (default) | Baseline — remember what is already on the IED; import nothing yet |
| New fault after baseline | Next poll creates event(s) for the new DR(s) |
| 25 new DRs at once | 10 this cycle, 10 next, 5 after that |
| Same DR again | Skipped (already in the fetched index) |
| Record fails 3 times | Skipped thereafter (fetch manually to see warnings) |

Off → on again → fresh baseline.

## 11.4 Scheduler

Server wakes about every 30 s and runs IEDs whose interval has elapsed (up to 4 IEDs in parallel).

Runs inside the API process — stops when you close ProtectionRCA.exe / the PC sleeps; resumes when the app starts again.

Check now forces one cycle immediately (409 if that IED is already checking).

## 11.5 Status on the card

| Line | Meaning |
| --- | --- |
| Last check | Age; “*N new · M record(s) on IED*” when OK |
| Next check | Next due time |
| Events created by auto-fetch | Running total |
| Baseline note | Until first check completes |
| Last check failed | Last error text |
| Scheduler warning | IEC61850_AUTO_FETCH false or library missing — Check now may still work |

## 11.6 Manual Fetch vs Auto-fetch

|  | Manual Fetch | Auto-fetch |
| --- | --- | --- |
| Who picks DRs | You (checkboxes) or “all new” on Fetch | Server: all new complete |
| Settings / SOE | Checkboxes | Checkboxes (defaults on) |
| SCL | Optional | No |
| Page open? | Yes | No |
| Multi-DR cap | Your selection | 10 per cycle |
| Audit | IEC61850_FETCH | IEC61850_AUTO_FETCH (user system) |

# 12. Event numbers

Every event has a readable, sequential identifier:

EVT-YYYY-NNNNN      e.g.  EVT-2026-00042

| Rule | Details |
| --- | --- |
| Year | Year the event was created |
| Sequence | Five-digit counter, restarts at 00001 each year |
| Allocation | Automatic for uploads, IEC 61850 fetch and auto-fetch — numbers are never reused within a year |
| Custom IDs | If an event was created with an explicit, meaningful ID (e.g. EVT-OC-132KV-FEEDER-001 from a package), it is kept |
| Legacy events | Events that had a random (UUID-style) ID from older versions are renumbered once, automatically, when the backend starts. The old ID is kept in the event’s extra data as previous_event_id, so old reports and notes can still be traced |

Use the event number in search (All events), reports, e-mails and review notes.

# 13. All events (list and filters)

Open Analysis → All events (route /events).

## Header actions

| Control | Purpose |
| --- | --- |
| Continue … | Resume last locally remembered event |
| Open Plant | Go to hierarchy / fetch / upload |
| Compare | Multi-event compare |
| Clear filters | Clears search, dates, and dashboard ?queue= filter |

When you arrive from a Dashboard KPI, a banner shows the active queue filter (e.g. Awaiting review).

## Search (live)

Type in Search. Matching is case-insensitive across:

Event number / ID (e.g. EVT-2026-000, 00042)

Substation / bay / relay (IED)

Feeder / description (fetched events contain “IEC 61850 fetch from …”)

Fault type and protection summary (e.g. 87T, 51N)

Status, decision state, data quality, severity

The counter shows “X of Y events”.

## Date range (From / To)

Uses the event date/time (falls back to created time if needed)

Times are interpreted in local browser time (no accidental UTC day-shift)

If To is left at midnight (00:00), the filter includes the entire calendar day

## Table columns

Event ID · Date/Time · Location (substation + bay) · Relay · Fault / element (protection primary, fault type secondary) · Status · Sev · DQ · Delete

## Empty / no-match states

| Situation | Message |
| --- | --- |
| No events in database | Prompt to open Plant and fetch/upload on an IED |
| Events exist but filters exclude all | “No events match…” + Clear filters |

# 14. Uploading files manually

## From the IED workspace (primary manual path)

Plant → expand to the IED → Open

Select Manual upload

Optionally type a description; drag and drop files (or click the zone to pick them); check the file chips

Click Upload, analyse & open summary (complete package) or Upload & create event (incomplete)

For a complete package: analysis starts and the Summary tab opens. For incomplete: open Files, add the missing COMTRADE/settings members, then Start analysis

Note SHA-256 on the event Files tab when you need integrity / chain of custody

Original files are stored immutably (content-addressed; not overwritten).

## From the event **Files** tab

After the event exists (uploaded or fetched):

Open the event → Files

Drag and drop additional members (settings, SOE, PDF, …)

Confirm upload, then Re-run analysis

## Supported extensions

.cfg .dat .cff .hdr .inf .csv .txt .xml .json .pdf .zip

plus vendor / settings packages:

.set .rdb .xrio .rio .eve .cev .log .dz5 .dex5 .d5z .pcmi .pcmp

and SCL files from IEC 61850 fetch (.cid .icd .scd, stored as attachments).

ZIP packages: uploading a .zip auto-extracts the archive. Each allowed member is stored as its own immutable event file. The original ZIP is kept as a PACKAGE attachment. Nested ZIPs expand (limited depth). Path-traversal / zip-bomb guards apply.

Vendor notes (honest):

| Format | Behaviour |
| --- | --- |
| SEL .rdb | OLE container — SET_ALL text extracted when present → settings ingest |
| SEL .cev | Converted to CFG+DAT for waveform / timeline use when convertible |
| DIGSI / PCM600 .dz5 / .dex5 / .d5z / .pcmi / .pcmp | Treated as ZIP-like packages when they contain nested COMTRADE / settings / CEV; proprietary non-ZIP blobs stay NOT CALCULABLE with export guidance |
| .set / .xrio / .rio / .eve / .log / SOE CSV | Parsed when structure is recognized; RIO/XRIO supply distance trip-zone geometry for R–X when present |

## Deleting an event

On All events → Delete, or open an event and click the trash icon (Delete event) in the header. Requires ANALYST (or higher). Confirm the dialog — the event and related DB records (including reports) are removed. Stored file blobs remain content-addressed (immutable storage); they are not rewritten. Browser “Continue” memory for that event is cleared. The Dashboard Events with reports and Total events counts drop on the next Dashboard refresh.

Deleting an event that was created by IEC 61850 fetch does not delete anything on the relay.

## Good practice

Upload CFG + DAT together (same base name when possible)

For CFF, upload the .cff

Or upload a ZIP / vendor package containing CFG/DAT/CFF (+ settings / SOE / PDF)

Upload under the correct IED so location / relay columns stay accurate

After upload, confirm Channel map and DR targets before trusting protection timing

Prefer originals from relay software — do not re-save in Excel

# 15. COMTRADE detection and validation

Open the event → COMTRADE tab.

| Field | Example meaning |
| --- | --- |
| Standard / revision | IEEE C37.111 1991 / 1999 / 2013 · IEC 2001 / 2013 |
| Container | CFG+DAT or CFF |
| Data format | ASCII, BINARY, BINARY32, FLOAT32 |
| Status | SUPPORTED / PARTIALLY_SUPPORTED / UNSUPPORTED |
| Channels / sample rate | From CFG metadata |

Validation statuses:

| Status | Meaning |
| --- | --- |
| VALID | Checks passed |
| VALID_WITH_WARNINGS | Usable — review warnings |
| PARTIALLY_SUPPORTED | Some features not fully validated (e.g. IEEE 1991 partial) |
| NOT_VALIDATED | Could not fully validate |
| INVALID | Do not trust results; fix source data |

The system does not silently interpolate missing samples or invent channels. Records fetched over IEC 61850 go through exactly the same detection and validation as uploaded ones.

# 16. Running analysis

After upload/fetch and validation (and preferably after Channel map / DR targets), start analysis from the event header (Start analysis / Re-run analysis). Fetched events with COMTRADE + settings, and auto-fetched events with *Start analysis automatically* on, are queued for you.

The API queues the job and returns immediately — engineering runs in the background so the browser does not time out.

Watch the Analysis progress panel and the status lamps:

COMTRADE · DATA · SETTINGS · PROTECTION · CONSISTENCY · RCA · REPORT

Each lamp is clickable and opens the tab that explains it (e.g. SETTINGS → Consistency / settings view, RCA → RCA tab).

Pipeline stages:

Upload → File Detection → COMTRADE Validation → Parsing →
Signal Processing → Event Reconstruction → Protection Analysis →
Consistency Checker → Fault Classification → RCA → Evidence → Report

Stage chips: ✓ completed · ● running · ○ pending · ✕ failed · – skipped. A progress bar shows overall completion. The progress panel is shown only while a job is queued or running (or failed); once analysis completes it disappears and the tabs show the results.

On parse/analyse the platform:

Persists COMTRADE file/channel metadata

Caches waveform samples for the Waveforms tab

Applies channel map + digital (DR target) map to electrical / timeline / protection

Runs consistency and RCA engines (scheme-aware where elements operate)

Indexes classical similarity features

Can generate an HTML report artefact

The Recommended next step banner guides the engineer (e.g. fix channel map, re-run after FAILED, open DR workspace).

If status is FAILED:

Hover the FAILED badge or open Details for the job error_message

Fix COMTRADE / channel map / DR targets / files as indicated

Click Re-run analysis

Prior results may still be viewable until the new run completes

Typical local analysis for normal records targets under ~2 minutes.

# 17. Event analysis workspace (detailed)

## Header band

| Element | Content |
| --- | --- |
| Breadcrumb | Substation › Bay › Relay |
| Title | Event number (e.g. EVT-2026-00042) and feeder |
| Date pill | Event date/time |
| Badges | Status · data quality · decision |
| Actions | Share pack · Start analysis / Re-run analysis · trash icon (Delete event) |
| Status lamps | COMTRADE · DATA · SETTINGS · PROTECTION · CONSISTENCY · RCA · REPORT (clickable) |

Below the band: the Recommended next step banner and, while a job runs, the Analysis progress panel.

## Tab bar

One tab bar that stays at the top while you scroll. Groups on the left, tabs of the selected group on the right:

| Group | Tabs |
| --- | --- |
| Setup | Overview · Files · COMTRADE · Channel map · DR targets |
| Analyse | DR workspace · Waveforms · Sequence · Electrical · Fault · Location |
| Protect | Protection · Consistency · RCA · Evidence |
| Conclude | Summary · Report · Review |

## Overview

Five engineering panels:

What happened — fault, inception, protection, consistency, RCA, DQ

Why — primary hypothesis with links to Evidence / RCA

Which setting — source, version, group, active group verification

What is uncertain — missing evidence, unverified settings, DQ, inconclusive items

What should I verify — deterministic recommended actions

Inputs loaded chips summarise what evidence files are present (COMTRADE package, settings, SOE / event report) in short engineer-readable phrases — useful before you trust protection timing or consistency.

Plant labels (substation / bay / relay) and bay one-line context can be saved from Overview. Fault distance shows NOT CALCULABLE when inputs are missing (never invented).

## Files

Uploaded / fetched originals, hashes, sizes, types (including extracted ZIP / vendor members and iec61850_settings_*.json / iec61850_soe_*.csv for fetched events). Add more files here.

## COMTRADE

Detection, validation, channel counts, sample rates, parser version.

## Channel map

Assign analog channel roles (phase currents/voltages, neutral, etc.). Wrong roles produce wrong RMS/phasors/impedance — fix here, then re-run analysis.

## DR targets (digital map)

Map digital channels to protection roles:

| Role | Typical use |
| --- | --- |
| PICKUP | Element pickup assert |
| TRIP | Trip / operate assert |
| 52A / 52B | Breaker auxiliary |
| RECLOSE | Auto-reclose |
| LOCKOUT | Lockout / 86 |
| UNKNOWN | Leave unmapped |

Optionally bind an element (21, 51, 51N, 67N, 87L, …). Rising-edge logic respects configured normal state. After save → Re-run analysis so Sequence / Protection / Consistency update.

## DR workspace

Combined disturbance-record view for day-to-day DR review: waveforms, cursors, phasors, R–X (faulted loop), harmonic bars, and harmonics heatmap. Upload `.rio` / `.xrio` with settings when you want trip-zone outlines on R–X.

## Waveforms

Interactive viewer with real sample arrays (from analysis cache / on-demand parse):

Zoom / pan / cursors

Channel selection · analog/digital

Markers when available

Engineering units

Inspect individual sample values — not smoothed-only curves.

## Sequence (timeline)

Chronological reconstruction (inception → pickup → trip → breaker → interruption → reclose/lockout when evidence exists).

| View | Use |
| --- | --- |
| Table | Relative time, Absolute time, device, digital/event, type, value, source |
| Cards | Engineer facts: element, target role, channel, state (0 → 1), baseline/threshold with units — not raw JSON dumps |

Absolute time

COMTRADE / DR digitals: CFG start_time + relative sample time (IEEE practice).

SOE rows: wall-clock from the SOE file (already absolute).

Settings vs observed timing strip at the top uses the earliest pickup / trip / 52a / interrupt from the timeline (case-insensitive). Expected columns stay blank when settings do not provide those times — values are never invented.

Digitals follow the DR targets map. Shared trip contacts such as `TRIP_CMD` (no ANSI code in the name) are attributed to the element that picked up just before the trip, so Summary Trips and Protection TRIP rows stay consistent with the DR.

External SOE / event-report points merge when parsers succeed — including iec61850_soe_<tag>.csv — only inside the DR time window (see [§10.7](#107-matching-soe--events-to-the-right-dr)).

## Electrical

RMS, phasors, sequences, power, impedance, harmonics, etc., each with method/quality. Missing → NOT CALCULABLE.

Impedance / fault resistance table — shows only the faulted loop for the classified fault (e.g. AG → Z_AG; ABG → Z_AB; ABC → Z_AB / Z_BC / Z_CA). Other loops may be computed internally but are not listed as “the” fault impedance.

R–X locus — plotted only when distance / 21 context applies and a fault type is classified. Points are the faulted loop only. Trip zones appear when RIO/XRIO geometry or scalar zone reaches are available from settings (never invented).

Harmonics — fault-window harmonic bars plus a time × order heatmap (short-time DFT) for phase currents when calculable.

Nominal voltage — Overview shows kV from the event field; if empty, analysis fills it from settings text, VT ratio, or …NNNkV… in filename/station name when present.

## Fault / Location

Fault type / characteristics and distance / location views when inputs exist. Distance never invented — NOT CALCULABLE with reason when CT/VT/line/settings are incomplete.

## Protection

Per-element table: Enabled · Pickup · Trip · Expected · Timing · Consistency · Setting source · Evidence.

See also [§18 Protection physics and schemes](#18-protection-physics-and-schemes).

## Consistency (critical)

Always read:

Overall status

Setting source / version

Active setting group (NOT VERIFIED if unknown)

| Status | Meaning |
| --- | --- |
| CONSISTENT | Observed matches expected under referenced settings |
| INCONSISTENT | Conflict — investigate; do not auto-confirm relay malfunction |
| UNVERIFIABLE | Cannot decide with available inputs |
| DATA_QUALITY_ISSUE | Record quality blocks the check |

Uploaded / fetched settings are auto-APPROVED and the active group marked VERIFIED by default (see [§20](#20-settings-and-setting-hierarchy)). You can still confirm or re-approve manually if your site policy requires it.

Mandatory rule: 51 Enabled = FALSE with pickup/trip observed → INCONSISTENT (typically HIGH). RCA remains INCONCLUSIVE regarding relay malfunction until active configuration is verified.

## RCA

Hypothesis board with status CONFIRMED / PROBABLE / POSSIBLE / UNLIKELY / INCONCLUSIVE, score, supporting / contradicting / missing evidence.

Scheme label (when detected) appears in the subtitle (e.g. stepped distance, feeder OC/EF, 87L+21).

Cause enrichment (field / asset): use the checkboxes on the RCA page (lightning evidence, vegetation field report, cable asset confirmed, …). Physical causes stay INCONCLUSIVE until these structured tokens are saved. After Save cause evidence, Re-run analysis.

CONFIRMED only when evidence requirements are met. Similarity and ML are supporting only. Zone / scheme mismatch → UNLIKELY for mismatched asset hypotheses.

Transformer internal (87T / 87RGF): CONFIRMED needs differential operate evidence and through_fault_excluded. The engine asserts through-fault exclusion when Id/Ir operate/restraint supports an internal fault, or (when winding phasors are missing) when 87T operated consistently without phase CT-sat / inrush indicators.

Decision vs RCA: A CONFIRMED primary hypothesis maps to ANALYSIS_COMPLETE unless material limitations remain (e.g. phase CT saturation POSSIBLE). Informational notes such as “Merged N external timeline events from SOE” do not downgrade the decision to WITH_WARNINGS. A PROBABLE primary still yields ANALYSIS_COMPLETE_WITH_WARNINGS.

## Evidence

RCA → Hypothesis → Finding → Calculation → Source → Raw data / file

## Summary / Report / Review

Summary consolidates the event story on a printable one-page sheet (fault, protection, consistency, RCA, quality).

| Field | Source |
| --- | --- |
| DR time | Relay disturbance time (COMTRADE trigger/start or stamped event time) — not upload/created time |
| Created | When the event was created in this app |
| Pickups / Trips | Asserted protection operations from analysis (PICKUP / TRIP). A row that tripped still shows as a trip; pickup remains visible from assessment details |
| OPERATED | Elements with trip asserted |

After a complete Manual upload or package-ready fetch, the app often lands here first. Report: see [§23](#23-reports-html-pdf-json). Both always render as a light “paper” page, even in dark theme.

| Review action | When to use |
| --- | --- |
| ACCEPT | Agree with automated findings |
| MODIFY | Accept with documented corrections |
| REJECT | Reject automated conclusions |
| INCONCLUSIVE | Cannot close with available evidence |
| REQUEST FIELD INVESTIGATION | Need field verification |

Automated results are retained; overrides are audited separately.

# 18. Protection physics and schemes

## Element 51 / 51N / 51P — time overcurrent

When pickup current, time dial (TMS), curve type, and measured current are available, the engine computes expected operate time using IEC/IEEE inverse curves, for example:

IEC Normal / Very / Extremely / Long-time Inverse

IEEE Moderately / Very / Extremely Inverse

Formula family: t = TDS × (A / (M^p − 1) + B) for multiple M > 1.

Earth-fault (51N) and phase (51P) variants use the mapped residual / phase quantities. If inputs are missing → timing physics status NOT_CALCULABLE. For fetched events, pickup / time dial / curve come from the relay’s PTOC settings.

## Element 67 / 67N / 67P — directional overcurrent

Directional assessments use available voltage/current phasor relationships and settings. Missing polarizing quantity → UNVERIFIABLE / NOT_CALCULABLE, never invented direction.

## Element 21 — distance

When apparent impedance and zone reach settings exist, a deterministic mho (default) or simple quad reach check evaluates zone entry. For fetched events, zone reaches come from the relay’s PDIS settings.

R–X display: uses the faulted loop impedance (phase–ground or phase–phase delta (V1−V2)/(I1−I2) as applicable). Zone outlines on the plot come from uploaded RIO / XRIO shapes or scalar Z1/Z2/Z3 reaches — never invented.

If impedance or reach is missing → NOT_CALCULABLE / fault distance not invented.

## Differential / BF (87L, 87T, 87B, 50BF)

Assessed when multi-end / winding / bus currents or BF timing evidence exist in the record or event meta. Insufficient inputs stay explicitly incomplete.

87 operate/restraint: when both-side currents exist, Id = |I1−I2|, Ir = (|I1|+|I2|)/2; trip expected if Id > Ip + k·Ir. The Protection tab can show an Id/Ir characteristic plot. Soft CT saturation cues use phase currents only (not residual IN alone).

## Scheme library (RCA context)

Deterministic scheme detection from operated/enabled elements and digital roles, for example:

Stepped distance (21)

Line differential + distance (87L + 21)

POTT / communication-aided schemes (when channel evidence exists)

Feeder overcurrent / earth-fault

Transformer / bus / generator unit schemes

Breaker-failure cascade

Scheme context influences RCA ranking; it does not invent trips or measurements.

# 19. Understanding status badges and quality labels

## Decision states

| State | Typical meaning |
| --- | --- |
| ANALYSIS_COMPLETE | Primary RCA CONFIRMED and no material analysis warnings |
| ANALYSIS_COMPLETE_WITH_WARNINGS | Primary is PROBABLE, or CONFIRMED with material warnings (e.g. phase CT sat) |
| ENGINEER_REVIEW_REQUIRED | Primary POSSIBLE / INCONCLUSIVE / UNLIKELY |
| INCONCLUSIVE | Forced by critical setting policy or no usable primary |
| DATA_INSUFFICIENT / UNSUPPORTED_FORMAT | Record/format blocks analysis |

Informational limitations (unused loops “NOT AVAILABLE”, SOE timeline merge notes, distance NOT APPLICABLE for feeder OC schemes) are listed for transparency but do not by themselves keep a CONFIRMED case in WITH_WARNINGS.

## Data quality

GOOD → ACCEPTABLE → WARNING → POOR → INVALID (+ NOT VALIDATED / UNSUPPORTED)

## Consistency

CONSISTENT · INCONSISTENT · UNVERIFIABLE · DATA_QUALITY_ISSUE

## Severity

INFO · LOW · MEDIUM · HIGH · CRITICAL

## IEC 61850 record status (browse table)

Complete · Incomplete · Already fetched

## Honest engineering labels

| Label | Meaning |
| --- | --- |
| NOT AVAILABLE | Signal/result absent |
| NOT VERIFIED | Setting group / source not independently verified |
| NOT VALIDATED | Format/feature not validated |
| NOT CALCULABLE | Missing inputs (e.g. distance) |
| INCONCLUSIVE | Evidence does not support confirmation |
| ML RESULT: NOT AVAILABLE | No approved classical ML model |
| SIMILARITY: NOT AVAILABLE | No comparable historical features yet |

# 20. Settings and setting hierarchy

Navigate settings from the event workspace (uploaded / fetched packages) and consistency panels. Version / group priority (highest first):

Event-specific active setting

Active setting group

Approved relay base setting

Relay configuration

Historical setting

Engineering design setting

The UI shows which source was used. The system never silently picks a group without displaying it.

## Settings from IEC 61850

When Settings is ticked during a fetch, iec61850_settings_<tag>.json is created from the relay data model (see [§10.6](#106-what-gets-created)). It is ingested like any other settings file:

The active setting group comes from LLN0.SGCB.ActSG, so it is known rather than assumed

Mapped values feed Protection / Consistency (pickups, time dials, curves, zone reaches, enables, CT/VT ratios)

Every raw attribute is preserved under iec61850_raw for audit

Vendor settings files found in the file store (e.g. SEL SET_*.TXT) are parsed as well

## Auto-approve uploaded settings (default)

When a settings file (JSON / text / vendor extract / .set / .xrio / .rio / IEC 61850 JSON, …) is loaded with the event, the platform treats it as:

Approval: APPROVED

Active group: VERIFIED

unless the package explicitly marks DRAFT / REJECTED / PENDING / PENDING_REVIEW.

Environment override: set AUTO_APPROVE_UPLOADED_SETTINGS=false to require manual Approve / Confirm active group again.

After changing this policy or uploading a new settings file, Re-run analysis so Consistency / Protection use the updated approval flags.

## Nominal system voltage from settings

If Overview shows UNKNOWN kV, analysis still tries to fill nominal_voltage_kv from:

Explicit JSON keys / asset fields

Settings text lines such as Nominal System Voltage : 132 kV

VT ratio primary (e.g. 132000/110 → 132 kV)

Filename or station name tokens such as 132kV

Never invents a voltage without one of these evidences.

# 21. Databases (auth vs plant/events)

Local / portable SQLite layout (under backend\):

| File | Contents |
| --- | --- |
| protection_rca_auth.db | Users, passwords, auth sessions |
| protection_rca_local.db | Plant hierarchy, events, event-number counters, IEC 61850 connection + auto-fetch settings per IED, analysis artefacts metadata |

Other folders under backend\:

| Folder | Contents |
| --- | --- |
| storage\ | Immutable file blobs (uploaded and fetched), reports |
| logs\ | api-launch.log — API console output written by the launcher |

## Why two databases?

Clearing plant/event data for a clean engineering trial does not wipe logins. You keep admin / other accounts while resetting events.

## How to clear data safely

Events and plant only (keep logins):

Stop ProtectionRCA.exe

Delete backend\protection_rca_local.db (and -wal / -shm if present)

Optionally delete backend\storage\ event/report blobs

Optionally clear browser localStorage key protection_rca_recent_events_v1 (Continue button)

Restart the exe — plant tree and events are empty (IED connections and auto-fetch settings are gone too); event numbers restart at 00001; log in as before

Full wipe including users:

Also delete backend\protection_rca_auth.db. Next start recreates bootstrap `admin` / `admin123` (or your BOOTSTRAP_ADMIN_* values).

Docker / PostgreSQL deployments use the configured application database; auth separation above applies to the local SQLite dual-DB mode.

# 22. Rules, models, and historical similarity

## Rules

Versioned packages (protection, consistency, RCA, fault). Activated versions apply to new analyses. Versions are stored with analysis for reproducibility.

## Models

Classical ML governance only (XGBoost / sklearn-class models if approved). No generative AI. Unapproved → ML RESULT: NOT AVAILABLE. ML never overrides deterministic evidence.

## Historical similarity

After analysis, classical feature vectors (voltage, frequency, DQ, fault/status hashes) are compared with cosine similarity.

Displayed as supporting evidence only

Never treated as proof of root cause

Optional future pgvector ANN index; classical path works on SQLite and PostgreSQL today

# 23. Reports (HTML, PDF, JSON)

Open event → Report.

| Format | How to get it |
| --- | --- |
| JSON | Structured sections in the report record |
| HTML | Download HTML — Jinja controlled templates / deterministic fallback |
| PDF | Download PDF — professional multi-section PDF built from the analysis payload (ReportLab Platypus): cover, inputs, electrical / protection summary, consistency, RCA, quality. Layout uses consistent page frames and human-readable labels — not a scraped HTML print |

The in-app preview is shown as a light page inside the workspace (its styles do not affect the rest of the application, and it stays readable in dark theme).

Regenerating a report for the same event updates that event’s report artefacts; the Dashboard Events with reports KPI still counts the event once (not once per format or regeneration).

API:

POST /api/reports with format: JSON | HTML | PDF

GET /api/reports/{id}/download

Report statements distinguish OBSERVED / CALCULATED / INFERRED / HYPOTHESIS. Every conclusion must be traceable to structured data — no LLM prose / generative AI.

Print remains available via the browser print dialog.

# 24. Users, SSO, and audit

## Users

Admins open Administration → Users to manage local accounts (auth database).

| Action | How |
| --- | --- |
| Add user | Add user → username, email, optional full name, role, active flag, password (min 8 characters) + confirm |
| Edit user | Row Edit → change email, name, role, active. Password fields are optional — leave blank to keep the existing password; if you type a new password, confirm it (min 8 characters) |
| Delete user | Row Delete → confirm. You cannot delete your own signed-in account. At least one admin should remain in operational use |

Roles: VIEWER, ANALYST, PROTECTION_ENGINEER, APPROVER, ADMIN (see [§4](#4-roles-and-permissions)).

## SSO

See [§3](#3-signing-in-local-and-sso). Configure AUTH_MODE, OIDC_ISSUER, OIDC_CLIENT_ID, OIDC_CLIENT_SECRET, OIDC_AUDIENCE on the backend.

## Audit

Open Administration → Audit (breadcrumb “Audit trail”).

| Column / control | Meaning |
| --- | --- |
| When | Local date/time |
| User | Username of whoever performed the action. Automatic actions (e.g. auto-fetch) show system |
| Action | Colour-coded chip: create = green, upload = blue, analyse = accent, update / review = amber, delete / clear = red, login / export = grey |
| Object | Object type and ID (event number, IED, …) |
| Details | Old → new values or parameters where applicable |
| Filter box | Filters by user, action, object or details text; the count shows matching entries |

Examples of audited actions:

Login (local or OIDC)

Upload

`IEC61850_FETCH` — manual fetch (host, records, files)

`IEC61850_AUTO_FETCH` — event created by auto-fetch

Analysis start / complete

Setting create / modify

Report generate / download

Engineer review / approval

Manual override

Event delete

Each entry: who / when / what / old→new where applicable.

# 25. Supported file types and COMTRADE matrix

| Extension | Typical content |
| --- | --- |
| .cfg / .dat | COMTRADE configuration + data |
| .cff | Combined COMTRADE file |
| .hdr / .inf | Header / information |
| .csv / .txt / .log | SOE / SER / event reports (when parsers exist), incl. iec61850_soe_*.csv |
| .xml / .json / .set / .xrio / .rio | Settings / configuration / trip-zone exports, incl. iec61850_settings_*.json |
| .rdb | SEL settings database (SET_ALL extract when present) |
| .cev | SEL compressed event — converted to CFG+DAT when convertible |
| .eve | Relay event report text (parsed when recognized) |
| .dz5 / .dex5 / .d5z / .pcmi / .pcmp | DIGSI / PCM600-style packages (ZIP-expand when possible) |
| .cid / .icd / .scd | IEC 61850 SCL — stored as attachment (reference only) |
| .pdf | Supporting attachment (reports, drawings, notes) — stored, not parsed as COMTRADE |
| .zip | Package archive — auto-extracted; allowed members processed further; ZIP kept as PACKAGE |

Detection prefers file contents, not extension alone. Proprietary non-extractable blobs are reported honestly (NOT CALCULABLE / unsupported) rather than silently invented.

Supported / regression-covered COMTRADE families (see docs/COMTRADE_SUPPORT.md for partial notes):

| Variant | Notes |
| --- | --- |
| IEEE C37.111-1999 / 2013 | Primary |
| IEEE C37.111-1991 | Partial support — fixtures included |
| IEC 60255-24:2001 / 2013 | Via aliases / detectors |
| ASCII · BINARY · BINARY32 · FLOAT32 | Parsers + golden fixtures |
| CFF | Detect / unpack path + fixture |

# 26. Sample / test / golden data

For training or regression (not production events):

test_data/comtrade/ieee_1999/ag_fault.cfg|.dat
test_data/comtrade/ieee_2013/mixed_event.cfg|.dat
test_data/comtrade/ieee_1991/ag_fault.cfg|.dat
test_data/comtrade/ieee_binary/
test_data/comtrade/ieee_binary32/
test_data/comtrade/ieee_float32/
test_data/comtrade/cff/ag_fault.cff
test_data/comtrade/malformed/
test_data/golden/

Training packages shipped in portable-share (each folder = one complete event: CFG + DAT + relay_settings.json + relay_base_settings.txt + relay_event_report.txt + soe.csv):

132kV_Feeder_Fault_Events/  EVT-AG-… · EVT-DIFF-… · EVT-DIST-… · EVT-OC-…132KV-FEEDER-001
220kV_Feeder_Fault_Events/  EVT-AG-… · EVT-DIFF-… · EVT-DIST-… · EVT-OC-…220KV-FEEDER-001

Use them via Manual upload (select all files in one folder, or zip the folder). They cover earth fault (AG), line differential, distance and overcurrent cases.

Regenerate synthetic matrix fixtures:

cd protection-rca
python scripts\generate_comtrade_fixtures.py

Create a plant path ending in an IED, upload test files on that IED, run analysis, and explore each tab.

# 27. Engineering language used in reports

Controlled templates only. Examples:

OBSERVED: trip digital was present

CALCULATED: apparent impedance entered Zone 1 reach

INFERRED: operation consistent with configured reach

HYPOTHESIS: internal feeder fault is probable

Never treat fluent wording as stronger than status badges.

# 28. Frequently asked questions

## General

Q: Where is Create event / Upload in the menu?

A: Removed on purpose. Go to Plant, build Substation → Voltage → Bay → Feeder → IED, then Open the IED and use Fetch from IED or Manual upload.

Q: How do I create my first event?

A: Plant → + Substation → + Voltage → + Bay → + Feeder → + IED → Open → either Fetch from IED (IP → Test connection → Browse IED → Fetch & create event) or Manual upload (drop CFG/DAT + settings or ZIP → Upload, analyse & open summary).

Q: Default login?

A: admin / admin123 on a fresh auth database. Change it for production.

Q: Can the tool trip a breaker or change settings?

A: No. OT control is disabled. IEC 61850 access is read-only.

Q: Does it use ChatGPT / generative AI?

A: No. Analysis and reports are deterministic / template-driven.

## IEC 61850 fetch

Q: Which relays can I fetch from?

A: Any IEC 61850 (Ed1 / Ed2 / Ed2.1) relay that exposes MMS file services — ABB/Hitachi, Siemens, GE, Schneider, SEL, NR, Toshiba, ZIV and others. Pick the vendor profile or leave Auto-detect.

Q: Test connection works but Browse finds no records.

A: If Test connection says “file services NOT available”, MMS file transfer is disabled in the relay configuration. Otherwise the records are probably in a vendor-specific folder — select the correct Vendor instead of Auto-detect. Also check the relay has actually recorded a disturbance.

Q: A record shows Incomplete.

A: The CFG or DAT is missing (often the relay is still writing it). Wait and Refresh list. Incomplete records cannot be analysed.

Q: Will fetching the same record twice create duplicates?

A: The browse list marks it Already fetched with a link to the event and does not pre-select it. Auto-fetch never re-imports a record it has already fetched.

Q: Why did my fetched event not start analysis?

A: Automatic start needs both COMTRADE and settings. If settings could not be read, add a settings file on the Files tab and click Start analysis.

Q: Does auto-fetch work when I close the browser?

A: Yes — it runs in the server. It does not run when the launcher/server is stopped.

Q: I switched on auto-fetch but old records were not imported.

A: By design the first check takes a baseline. Switch auto-fetch off, tick Also import records already on the IED, and switch it on again — or fetch old records manually.

Q: Which PC connects to the relay when colleagues use the LAN URL?

A: The host PC running the application. It needs network access to the relays on port 102.

## Events and numbering

Q: My old events have new numbers.

A: Events with random (UUID) IDs from older versions were renumbered to EVT-YYYY-NNNNN at the first start of this version. The old ID is stored as previous_event_id.

Q: I deleted the local DB and cannot log in

A: You deleted protection_rca_auth.db as well. Restart the app to recreate bootstrap admin, or keep auth DB and only delete protection_rca_local.db when clearing events.

Q: Why are Location / Relay / Fault columns empty?

A: Upload / fetch under an IED so plant labels attach; complete analysis for fault / protection columns.

Q: Search on All events does nothing useful

A: Type any fragment of event number, station, bay, relay, fault, or protection code (e.g. EVT-2026, IED-4, Bay 1, 51N). Use From/To for dates. Clear filters resets.

Q: Can I delete an event?

A: Yes — All events Delete, or the trash icon in the event header (ANALYST+). Confirm first. Nothing on the relay is affected. Dashboard Total events and Events with reports drop after the next Dashboard refresh.

Q: Why did “Events with reports” change when I deleted an event?

A: By design. The KPI counts current events that have a report, not historical file generations. Delete the event → its reports go with it → the count falls.

Q: KPI click does nothing useful

A: It opens All events with a queue filter (e.g. Events with reports). Use Clear filters to reset.

Q: Continue button still shows a deleted event

A: Refresh the page after delete; the app prunes recent-event memory when the event is gone. You can also clear localStorage key protection_rca_recent_events_v1.

## Analysis

Q: Why is RCA INCONCLUSIVE?

A: Consistency findings (e.g. disabled 51 operating), or missing evidence for CONFIRMED.

Q: Why does Decision say WITH_WARNINGS when RCA is CONFIRMED?

A: Only material warnings downgrade a CONFIRMED case. Re-run analysis on events created with older versions.

Q: Why does the impedance table show only one Z row?

A: By design — only the faulted loop for the classified fault.

Q: Why is Nominal UNKNOWN kV?

A: No voltage evidence was found. Upload/fetch settings that state nominal kV (or a VT ratio), then Re-run analysis.

Q: Do I still need to Approve settings?

A: Not by default — uploads/fetches are auto-APPROVED / active group VERIFIED. Set AUTO_APPROVE_UPLOADED_SETTINGS=false to restore manual approval.

Q: Fault distance NOT CALCULABLE

A: Needs validated CT/VT, line parameters, and impedance model — never invented.

Q: Waveforms empty

A: Run analysis after upload so samples are parsed and cached; check COMTRADE validation.

Q: Why is analysis FAILED but older results still visible?

A: The latest background job failed. Hover FAILED / open Details, fix inputs, Re-run analysis.

Q: Lightning / vegetation / cable stay INCONCLUSIVE

A: Protect → RCA, tick the matching cause enrichment evidence, save, Re-run analysis.

Q: Pickup / trip times look wrong

A: Setup → DR targets, map the correct digitals (and element), save, re-run.

Q: Electrical / distance looks wrong after auto-detect

A: Setup → Channel map, correct roles, save, re-run.

Q: Can I upload a ZIP of CFG/DAT? SEL `.rdb` / `.cev`? DIGSI / PCM600?

A: Yes where extractable (see [§14](#14-uploading-files-manually)). Opaque proprietary blobs stay unsupported — export CFG/DAT from the vendor tool.

Q: How do I get a PDF?

A: Event → Report → Download PDF. The PDF is built from the analysis sections (professional layout), not a screenshot of the HTML page.

Q: How do I fetch several disturbance records at once?

A: List records on IED → tick the ones you want (or Select all new) → Fetch DR + settings / events. Or click Fetch without listing — all new complete DRs are taken. One event per DR.

Q: Does auto-fetch also pull settings and SOE?

A: Yes, when the Settings and Events toggles are on (defaults). Each new DR gets its own event with COMTRADE + those extras. SCL is manual-fetch only. See [§11](#11-automatic-fetch-auto-fetch).

Q: The IED has a huge SOE — will every row land on my event?

A: No. SOE is matched to the DR by filename and/or time window (CFG start − 5 s … end + 30 s). See [§10.7](#107-matching-soe--events-to-the-right-dr).

Q: Browse finds no COMTRADE — how do I set the path?

A: Enable MMS file transfer in the relay tool, then set COMTRADE path on IED (often /COMTRADE/) from that tool or the manual. Paths are not downloaded from the internet.

Q: Summary says Trips “None asserted” but the Sequence shows TRIP_CMD

A: Re-run analysis on a build that attributes shared trip contacts to the picking-up element. Map opaque channels under DR targets if needed.

Q: DR time vs Created on Summary / dashboard?

A: DR time = disturbance on the relay (COMTRADE). Created = when this app created the event.

Q: After manual upload I landed on Summary — is that normal?

A: Yes, when COMTRADE and settings were present. Analysis started automatically and Summary is the first place to read the story. Use the tab bar for Waveforms, Consistency, Report, etc.

Q: How do I add or remove users?

A: ADMIN → Users → Add user, or Edit / Delete on a row. On edit, leave password blank to keep the current one. You cannot delete yourself.

## Portable / sharing

Q: Does the other PC need Python?

A: No. portable-share\python\ contains the complete runtime. Share the whole portable-share folder (zipped), not only the exe.

Q: Can I give only ProtectionRCA.exe to a colleague?

A: No. They need the full `portable-share` folder (exe + python + backend + frontend\dist + rules + scripts). Build it with scripts\build-portable-share.bat.

Q: How do others open the app from my laptop?

A: Start the exe on your PC, allow Firewall if asked, then they open the LAN URL shown in the control window (e.g. http://192.168.x.x:8001/). Do not share 127.0.0.1 with them.

Q: Browser opens 8001 or 5173 — which is correct?

A: 8001 = portable (built UI served with the API). 5173 = developer Vite UI. Both use the API on 8001.

Q: Closed browser but ports busy

A: Close the launcher control window (Stop & Close).

Q: SSO button missing

A: OIDC not enabled on the API (AUTH_MODE still local).

# 29. Troubleshooting

## Start-up / portable

| Symptom | What to check |
| --- | --- |
| Exe says backend/frontend not found | Run ProtectionRCA.exe from inside protection-rca or portable-share; keep python\, backend\, frontend\ next to it |
| “API did not start on port 8001” | Read the log tail shown in the message, or open backend\logs\api-launch.log. Common causes below |
| Log says Python / module not found | The folder is incomplete or from an old build. Rebuild with scripts\build-portable-share.bat and copy the whole folder again |
| Old build message about a missing base Python / .venv | You are running a portable folder built before 0.7.0 (it depended on the builder’s Python). Rebuild — the new build bundles python\ |
| Log says address already in use | Another copy is running, or another program uses port 8001. Close other ProtectionRCA.exe windows (Task Manager if needed) or set PROTECTION_RCA_PORT |
| Message mentions a different port (e.g. 8011) | PROTECTION_RCA_PORT is set in the environment. Remove it or open that port’s URL |
| First start very slow / times out | Antivirus scanning python\ on first launch. Wait and start again; add an exclusion if allowed |
| Database locked | Another process has protection_rca_local.db open (second copy, sync tool such as OneDrive). Close it / move the folder out of synced locations |
| UI blank / API errors | http://127.0.0.1:8001/health |
| Colleague cannot open LAN URL | Same Wi-Fi/LAN; use host IP not 127.0.0.1; allow Windows Firewall private network for port 8001 |
| Exe rebuild “Access denied” / false “EXE OK” | Close all ProtectionRCA.exe windows. Prefer scripts\build-all-latest.bat — it kills locked processes and fails if PyInstaller cannot write the EXE |
| Build stops at “bundled Python check failed” | The builder machine’s backend\.venv is missing packages. Run pip install -r backend\requirements.txt in the venv and rebuild |

## IEC 61850 fetch

| Symptom | What to check |
| --- | --- |
| Panel warns the IEC 61850 library is missing / HTTP 503 | Install pyiec61850-ng (pip install -r backend\requirements.txt) or use a current portable build |
| Test connection times out / refused (HTTP 502) | Wrong IP; VLAN/firewall; TCP 102 blocked; MMS client slots full; IEC 61850 server disabled on the relay |
| Access denied | Allow the host PC’s IP / MMS auth in the relay tool |
| Browse finds no records | Enable MMS file transfer; set COMTRADE path on IED; choose Vendor; confirm the relay has records |
| Browse takes very long / times out (~90 s) | Large file store — set COMTRADE path or vendor profile |
| Record Incomplete | CFG/DAT still writing — Refresh list later |
| Fetch completes with warnings | Open the warnings list; event still holds what was retrieved |
| “No complete disturbance records…” | Nothing complete to fetch with settings/events — list first and check Status |
| Settings JSON almost empty | Upload vendor settings export on Files if the data model exposes little |
| Event did not auto-analyse | Settings missing → add settings, Start analysis |
| Wrong SOE on an event | Confirm DR time; re-fetch / re-analyse so the time window applies ([§10.7](#107-matching-soe--events-to-the-right-dr)) |

## Auto-fetch

| Symptom | What to check |
| --- | --- |
| “Enter the IED IP address before enabling…” | Fill IP in Relay connection first |
| “Background scheduler is not running…” | IEC61850_AUTO_FETCH false or library missing — use Check now |
| Nothing imported after enabling | Expected (baseline). New DRs after that import. Use *Also import records already on the IED* for backlog |
| Only some of many new DRs appeared | Max 10 per cycle — wait for the next interval |
| Settings/SOE missing on auto events | Turn Settings / Events on (only editable while auto-fetch is off) |
| Last check failed | Same as Test connection; retries next interval |
| A record is never imported | Failed 3 times — fetch manually |
| “already running” (409) | Wait for the in-flight check |
| Auto-fetch stopped overnight | Launcher/PC off or asleep — server must stay running |

## Analysis and data

| Symptom | What to check |
| --- | --- |
| Cannot log in after DB clear | Ensure protection_rca_auth.db exists or restart for bootstrap admin / admin123 |
| No Create event menu | Use Plant → IED → Fetch from IED / Manual upload |
| Search finds nothing unexpected | Clear filters; confirm spelling; protection codes like 87T are searchable |
| Date filter misses events | Leave To at 00:00 to include whole day; times are local |
| Settings NOT VERIFIED / WITH_WARNINGS on old events | Re-run analysis after upgrading |
| Upload rejected | Extension, size limit, or role; upload from IED workspace or event Files |
| COMTRADE INVALID | Fix source export; do not force confident RCA |
| Analysis FAILED | Hover FAILED for error_message; fix Channel map / DR targets / files; Re-run; restart exe after backend updates |
| Stuck “Queued (background)” with FAILED | Latest job never advanced — re-run after fix; check backend\logs\api-launch.log |
| Waveforms empty | Analysis/parse not run or validation failed |
| Wrong pickup/trip sequence | Setup → DR targets → save → re-run |
| Wrong phasors / distance | Setup → Channel map → save → re-run |
| Consistency empty | Analysis not run or no digital/setting inputs |
| Vendor .rdb / .cev / DIGSI unused | Confirm extract succeeded on Files tab; else export CFG/DAT + settings text from vendor tool |
| PDF download fails | Ensure reportlab installed in backend env (included in portable build) |
| Report shows “Report template NOT AVAILABLE” | The templates\ folder is missing next to backend\ (portable folders built before this fix). Rebuild portable-share or copy protection-rca\templates into it, restart the exe, then click Refresh report |
| Cannot review | Role below PROTECTION_ENGINEER / APPROVER |
| Audit shows “system” | Automatic action (e.g. auto-fetch) — not a missing user |

API docs: http://127.0.0.1:8001/docs

# 30. Where to find more documentation

| Document | Content |
| --- | --- |
| README.md | Install, launch, overview |
| docs/IMPLEMENTATION_STATUS.md | Honest feature status vs specification |
| docs/ARCHITECTURE.md | System design |
| docs/API.md | REST endpoints |
| docs/COMTRADE_SUPPORT.md | Format support matrix |
| docs/PROTECTION_RULES.md | Protection rule engine |
| docs/CONSISTENCY_CHECKER.md | Consistency logic |
| docs/RCA_ENGINE.md | Hypothesis scoring |
| docs/ENGINEERING_LIMITATIONS.md | Explicit non-claims |
| docs/SECURITY.md | Auth, RBAC, OT read-only |
| docs/TESTING.md | Tests / golden data |
| docs/DEPLOYMENT.md | Docker / AWS notes |
| docs/DATABASE.md | Schema notes |

IEC 61850 REST endpoints (see /docs for schemas):

| Method + path | Purpose |
| --- | --- |
| GET /api/iec61850/info | Library availability, vendor profiles |
| GET / PUT /api/ieds/{id}/iec61850 | Saved connection (IP, port, vendor, remote_directory) |
| POST /api/ieds/{id}/iec61850/test | Connect + nameplate |
| POST /api/ieds/{id}/iec61850/browse | List records (+ searched / discovered dirs) |
| POST /api/ieds/{id}/iec61850/fetch | Fetch DRs + optional settings/SOE/SCL; create event(s) |
| GET / PUT /api/ieds/{id}/iec61850/auto-fetch | Auto-fetch settings and status |
| POST /api/ieds/{id}/iec61850/auto-fetch/run-now | Check now |

Word copies of this guide:

docs/Protection_RCA_User_Guide.docx

docs/Protection_RCA_User_Guide.doc

Project root copies with the same names

Regenerate Word files after editing this Markdown:

cd protection-rca
python scripts\export_user_guide_doc.py

# 31. Quick reference card

START      → Double-click ProtectionRCA.exe (portable: :8001 · dev: :5173)
STOP       → Close launcher control window
SHARE      → scripts\build-portable-share.bat → zip whole portable-share\
             (Python bundled — nothing to install on the other PC)
API FAIL   → Read log tail / backend\logs\api-launch.log
LAN        → Others open http://<host-IP>:8001/ (Firewall allow)
LOGIN      → admin / admin123 (bootstrap) or SSO if configured
PLANT      → Substation → Voltage → Bay → Feeder → IED → Open
FETCH      → IED → Fetch from IED → IP [/ COMTRADE path] → Test
             → List records → tick (Select all new) → Fetch DR + settings / events
             → One event per DR; SOE matched by time / filename
AUTO       → Auto-fetch ON → interval → baseline first, then new DRs (max 10/cycle)
             → Settings + Events toggles ride with each DR
UPLOAD     → IED → Manual upload → CFG/DAT/CFF/ZIP + settings
             → Upload, analyse & open summary (or Upload & create event)
EVENT ID   → EVT-YYYY-NNNNN (auto) · legacy UUID → previous_event_id
MAP        → Setup → Channel map + DR targets → save
ANALYSE    → Auto on complete package, or Start / Re-run → status lamps
SUMMARY    → DR time vs Created · Pickups / Trips · one-page story
SEQUENCE   → Table or Cards · Absolute = CFG start + relative (DR)
VERIFY     → Waveforms → Sequence → Consistency → RCA → Evidence
CAUSE      → RCA cause enrichment (field evidence) → re-run
FILTER     → All events: Search + From/To + Clear filters
DASHBOARD  → Events with reports = live events with a report
REPORT     → Download HTML or professional PDF
USERS      → ADMIN → Users → Add / Edit / Delete (password optional on edit)
CLOSE-OUT  → Review (ACCEPT / MODIFY / REJECT / …)
DELETE     → All events → Delete, or trash icon in event header (ANALYST+)
AUDIT      → Administration → Audit (filter; "system" = automatic)
DBS        → auth.db = users · local.db = plant/events/IED connections
REMEMBER   → Read-only IEC 61850 · No invented data · No OT control · No generative AI

*End of User Guide — Protection RCA Platform (document version 0.9.0)*