## Complete RCA Matrix
Asset/System | RCA Scenario | Protection Functions / ANSI Examples | LEVEL 1 - Primary Relay Evidence | LEVEL 2 - SOE / Event Evidence | LEVEL 3 - DR / Physical Evidence | FALLBACK PATH - If Primary Evidence Missing | Final RCA Classification
Transformer | Normal energization | Inrush / energization detection; differential supervision; switching logic | No sustained fault declaration; energization/start state recognized | CB CLOSE → energization → transient → stable state | Initial asymmetric magnetizing current followed by decay; no sustained fault signature | If dedicated inrush/start signal missing: CB-close timestamp + current waveform asymmetry/decay + voltage recovery + absence of persistent fault | NORMAL ENERGIZATION
Transformer | Energization inrush | Inrush detector; transformer differential; overcurrent | Inrush indication if available; differential may transiently respond | CB CLOSE → current surge → protection response/blocking → reset/stable state | Large asymmetric/distorted magnetizing current, decay after energization; harmonics if available | If inrush bit/harmonic channel missing: waveform timing + asymmetry + decay + CB close; harmonic evidence is supporting, not mandatory | PROBABLE/CONFIRMED INRUSH
Transformer | Internal phase fault | Transformer differential; phase OC; distance where applicable | Differential/phase protection operates with phase information if available | Protection pickup → trip → lockout/master trip if applicable → transformer CB(s) open | Sustained differential/fault current, affected phase voltage depression | If differential signal missing: phase OC + both-side currents + voltages + topology + neighboring relay evidence | INTERNAL / IN-ZONE PHASE FAULT
Transformer | Internal earth fault | REF/earth fault/differential | Earth/differential protection operates | Earth-fault pickup → trip → breaker opening | Residual/neutral current and phase-earth voltage behavior | If dedicated earth/REF signal missing: derive residual current from three-phase currents + neutral current if available + topology | INTERNAL / IN-ZONE EARTH FAULT
Transformer | External through fault | Phase/earth OC; directional OC; transformer differential restraint | OC/earth protection may operate; differential should normally restrain | External feeder/bus protection sequence → transformer protection response → breaker clearing | High through-current on both sides with differential current restrained relative to through-current | If restraint/differential data unavailable: compare both-side currents, direction, sequence components, voltage depression and topology | EXTERNAL / OUT-OF-ZONE FAULT
Transformer | Differential operation caused by CT saturation / measurement issue | Differential; OC; CT supervision | Differential operates without convincing internal-fault declaration from independent evidence | Differential trip occurs during external/high-current event | High through-current + distorted/clipped CT waveform + temporary current mismatch | If CT saturation flag unavailable: raw waveform distortion + both-side current comparison + external fault sequence | CT SATURATION / INSTRUMENTATION SUSPECTED
Transformer | Overfluxing / overexcitation | Overfluxing / V/Hz protection | Overfluxing stage operates | Pickup → timer/alarm/trip → system response | Elevated V/Hz; voltage and frequency relationship supports event | If dedicated stage/frequency signal missing: derive V/Hz from voltage waveform and frequency | OVEREXCITATION / OVERFLUXING
Transformer | Thermal overload | Thermal model / overload / temperature protection | Thermal alarm/trip | Thermal pickup → delay → alarm/trip → load change | Sustained RMS current and/or temperature rise | If thermal element unavailable: RMS current trend + RTD/temperature + loading duration | THERMAL OVERLOAD
Motor | Normal starting | Start supervision / motor-start element | Start state recognized; no fault protection trip | CB CLOSE → start detection → acceleration → start supervision reset | High starting current followed by expected decay/acceleration | If start element absent: CB close + current envelope + speed/process feedback if available | NORMAL START
Motor | Prolonged starting | Start supervision / overload / locked-rotor | Start timer remains active or start-time limit reached | CB CLOSE → high current persists beyond expected start window → alarm/trip | Starting current remains high with insufficient decay/acceleration | If timer bit absent: duration of elevated current + speed/auxiliary evidence | PROLONGED START
Motor | Locked rotor | Locked-rotor / start protection | Locked-rotor element or start timeout operates | Start → high current persists → locked-rotor/start timeout → trip | Near-constant high current with little/no acceleration evidence | If locked-rotor bit absent: current duration + absence of speed increase + thermal rise | LOCKED ROTOR
Motor | Load jam during running | Jam / stall / overload protection | Jam/stall element operates | Running state → current rises → jam detection → trip | Sudden sustained current increase from running state | If jam element absent: current step/rise + running-state SOE + speed/process feedback | LOAD JAM
Motor | Thermal overload | Thermal model / overload | Thermal stage operates | Thermal pickup → delay → trip | Sustained RMS current and temperature/thermal accumulation | If thermal signal absent: current trend + temperature + duration | THERMAL OVERLOAD
Motor | Phase loss / discontinuity | Phase-loss / negative-sequence / phase monitoring | Phase-loss/discontinuity element operates | Detection → timer → alarm/trip | One phase current/voltage abnormal relative to others | If dedicated element absent: compare IA/IB/IC and VA/VB/VC; derive negative sequence | PHASE LOSS / DISCONTINUITY
Motor | Negative-sequence unbalance | Negative-sequence protection | Negative-sequence stage operates | Pickup → timer/thermal limit → trip/alarm | Elevated I2/I1 and phase unbalance | If element absent: calculate sequence components from synchronized three-phase current waveforms | NEGATIVE-SEQUENCE / UNBALANCE
Motor | Internal phase fault | Motor differential / phase OC | Differential or phase fault protection operates | Pickup → trip → motor CB open | High fault current, voltage depression, differential imbalance | If differential unavailable: phase OC + current/voltage waveform + feeder topology | INTERNAL MOTOR PHASE FAULT
Motor | Internal earth fault | Earth fault / differential / sensitive earth fault | Earth/differential protection operates | Pickup → trip → breaker opening | Residual current / zero-sequence behavior + phase-earth voltage response | If dedicated earth element absent: derive residual current from phase currents + topology | INTERNAL MOTOR EARTH FAULT
Feeder/Line | Phase-earth in-zone fault | Earth fault; directional earth fault; distance | Earth/directional/distance protection operates | START → timer/zone → trip → CB open | 3I0/residual current + phase voltage depression; direction/impedance supports protected zone | If zone/direction signal missing: phasors + sequence components + impedance trajectory + topology | IN-ZONE PHASE-EARTH FAULT
Feeder/Line | Phase-phase in-zone fault | Phase OC; directional OC; distance | Phase protection operates | START → timer/zone → trip | Two phase currents rise; corresponding voltages depress; negative sequence increases | If zone signal absent: calculate apparent impedance and inspect phase current/voltage relationship | IN-ZONE PHASE-PHASE FAULT
Feeder/Line | Three-phase in-zone fault | Phase OC; directional OC; distance | Phase protection operates | START → zone/timer → trip | Three-phase current rise + voltage depression | If distance/zone bit absent: V/I phasors + impedance trajectory + topology | IN-ZONE 3-PHASE FAULT
Feeder/Line | External / out-of-zone fault | OC; directional OC; distance | Relay sees fault current but direction/zone may restrain | Neighboring protection/backup sequence indicates external location | High current with direction/impedance inconsistent with protected zone | If directional/zone data missing: topology + neighboring relay SOE + current/voltage comparison | OUT-OF-ZONE FAULT
Feeder/Line | High-impedance fault | High-impedance fault detection; sensitive earth fault | Special HIF/HIZ element may operate; conventional OC may not | Detection → alarm/trip if configured | Low/moderate fault current, abnormal residual/sequence signature, possible intermittent behavior | If dedicated HIF element absent: residual/sequence current + voltage distortion + intermittent waveform pattern | PROBABLE HIGH-IMPEDANCE FAULT
Feeder/Line | Intermittent / transient earth fault | Transient/intermittent earth-fault detection | Transient earth-fault element may operate | Repeated short pickups/operations around intermittent events | Short residual-current bursts with repeated extinction/restrike behavior | If dedicated signal absent: identify repeated synchronized 3I0/residual bursts + voltage disturbance | INTERMITTENT EARTH FAULT
Feeder/Line | Temporary fault cleared by autoreclose | Auto-reclose + fault protection | Protection trips; autoreclose operates | Trip → CB OPEN → dead time → CB CLOSE → no repeat trip | Fault signature exists before first opening and disappears after reclose | If autoreclose bit absent: infer from CB open/close SOE and disappearance of fault signature | TEMPORARY FAULT / SUCCESSFUL RECLOSURE
Feeder/Line | Persistent fault after autoreclose | Auto-reclose + fault protection | Protection operates again after reclose | Trip → open → reclose → protection pickup/trip again | Fault signature persists after reclose | If autoreclose signal absent: repeated CB open/close + repeated protection operation | PERSISTENT FAULT / UNSUCCESSFUL RECLOSURE
Feeder/Line | Switch onto fault | Switch-onto-fault / instantaneous protection | Fault protection operates immediately following close | CB CLOSE → immediate protection pickup/trip | Fault current and voltage collapse start essentially at energization | If dedicated SOTF logic absent: CB close timing + immediate fault waveform | SWITCH-ONTO-FAULT
Busbar | Internal bus fault | Bus differential; bus overcurrent | Bus differential operates; multiple zones/feeders may trip | Bus protection trip → lockout/master trip → multiple breakers open | Simultaneous current contributions from multiple circuits + bus voltage collapse | If bus differential bit absent: correlate multiple feeder/incomer currents, directions, bus voltage and breaker SOE | INTERNAL BUS FAULT
Busbar | External feeder fault with bus restraint | Bus differential + feeder protection | Feeder protection operates; bus differential should remain restrained | Feeder trip → feeder CB opens while bus remains energized | High feeder current but no credible bus-wide differential fault | If bus differential data missing: feeder current + bus voltage + other breaker states + neighboring relay SOE | EXTERNAL FEEDER FAULT
Busbar | Bus differential false operation / CT issue | Bus differential; CT supervision | Bus differential trip without matching physical bus fault | Multiple breakers trip but event sequence does not match a bus fault | No credible bus-fault waveform; CT mismatch/distortion possible | If CT diagnostic unavailable: compare all CT waveforms, current balance/polarity and external-fault sequence | BUS PROTECTION MALOPERATION / CT ISSUE
Generator | Internal stator phase fault | Generator differential; phase OC | Differential/phase protection operates | Pickup → trip → generator breaker opens | High differential/fault current + terminal voltage depression | If differential unavailable: phase OC + current/voltage + sequence + topology | INTERNAL STATOR PHASE FAULT
Generator | Stator earth fault | Earth fault; generator differential; neutral/third-harmonic schemes | Earth-fault scheme operates | Pickup → trip → breaker opening | Residual/neutral/third-harmonic evidence depending protection scheme | If dedicated element absent: residual current + neutral/terminal voltage + third harmonic if recorded | STATOR EARTH FAULT
Generator | Loss of excitation / underexcitation | Underexcitation / loss-of-field | Underexcitation protection operates | Pickup → delay → alarm/trip | P/Q and V/I operating trajectory consistent with loss of excitation | If dedicated signal absent: P/Q + phasor trajectory + voltage/power-angle behavior | PROBABLE LOSS OF EXCITATION
Generator | Negative-sequence heating | Negative-sequence protection | Negative-sequence stage operates | Pickup → thermal/timer → trip | Elevated I2 and sustained phase unbalance | If element absent: calculate I2/I1 from three-phase currents | NEGATIVE-SEQUENCE CONDITION
Generator | Under/overfrequency | Frequency protection; df/dt; load shedding | Frequency stage operates | Frequency pickup → timer/load shedding/trip | Frequency excursion and rate-of-change | If relay frequency unavailable: derive frequency and df/dt from voltage waveform | FREQUENCY EVENT
Generator | Out-of-step / pole slip | Out-of-step / vector-shift | Out-of-step/vector-shift element operates | Detection → trip/blocking logic → breaker response | Impedance/power-angle trajectory or voltage-vector shift behavior | If dedicated element absent: impedance trajectory + P/Q oscillation + voltage-angle behavior | OUT-OF-STEP
Generator | Accidental energization | Accidental energization/start protection | Dedicated logic/protection operates | CB CLOSE while generator is not in expected state → immediate protection response | Current appears immediately after unexpected energization; machine pre-event state inconsistent with normal operation | If dedicated logic absent: CB close + pre-event machine state + current surge + voltage response | ACCIDENTAL ENERGIZATION
Generator | Overfluxing | V/Hz / overexcitation | Overfluxing stage operates | V/Hz pickup → timer → trip/alarm | Elevated V/Hz | If stage absent: derive V/Hz from voltage waveform and frequency | OVERFLUXING
Capacitor Bank | Normal switching transient | Switching logic; voltage/current supervision | No sustained fault declaration | CB CLOSE → transient → decay → stable | Short-duration oscillatory/high-frequency transient synchronized with switching | If switching signal absent: CB SOE + waveform onset/decay | NORMAL SWITCHING TRANSIENT
Capacitor Bank | Capacitor unbalance / internal fault | Unbalance; overcurrent; earth fault | Unbalance/fault protection operates | Pickup → alarm/trip → CB open | Phase/current/neutral imbalance or sustained abnormal voltage/current | If dedicated unbalance signal absent: calculate phase/neutral imbalance from DR | CAPACITOR UNBALANCE / INTERNAL FAULT
Capacitor Bank | Overvoltage | Overvoltage / sequence-voltage protection | Overvoltage stage operates | Pickup → delay → trip/alarm | Sustained elevated voltage | If protection bit absent: calculate RMS and sequence voltages from DR | OVERVOLTAGE CONDITION
Breaker | Normal successful operation | Trip command; breaker status; current interruption | Trip command issued; status changes normally | Trip command → 52a/52b transition → current interruption | Current drops to zero after expected opening; breaker status agrees | If breaker status unavailable: current interruption + neighboring device SOE + voltage/state change | BREAKER SUCCESSFUL
Breaker | Breaker fails to open after trip | Breaker failure / backup breaker logic | Breaker-failure element operates if available | Primary trip command → expected clearing time expires → current persists → backup trip | Fault current persists after local trip command; local status fails to change | If BF bit absent: trip command + persistent current + unchanged status + subsequent upstream breaker trip | BREAKER FAILURE / LBB
Breaker | Trip circuit failure | Trip-circuit supervision / breaker monitoring | Trip-circuit alarm/supervision may operate | Trip command issued but no expected breaker response | No current interruption and/or breaker status unchanged; DC/trip voltage abnormal if recorded | If supervision signal absent: command/status mismatch + current persistence + DC/trip voltage if available | TRIP CIRCUIT / CONTROL FAILURE
Breaker | Breaker stuck / mechanical failure | Breaker monitoring; breaker failure | Failure to open or close as commanded | Command → no status transition within expected time | Current/state remains inconsistent with command | If dedicated monitoring absent: SOE command/status mismatch + current/voltage evidence | BREAKER MECHANICAL/CONTROL FAILURE
System | Local Breaker Backup / LBB cascade clearing | Breaker failure + backup protection + lockout | Local BF/LBB function starts or operates | Primary feeder/transformer breaker trip command → local CB fails → BF timer → upstream/incomer/bus-side breakers trip | Fault current persists after primary trip and disappears only after backup breakers open | If BF/LBB signal absent: reconstruct using trip command, 52 status, current persistence, BF timer-equivalent interval and upstream breaker trips | FAULT + LOCAL BREAKER FAILURE + LBB/CASCADE CLEARING
System | Cascade trip caused by protection coordination | Primary protection + backup protection | Primary protection may fail/block; backup stage operates | Primary device → no/failed clearing → backup relay operates → additional breaker(s) trip | Fault persists through first clearing attempt and clears after backup device operation | If backup stage signal absent: SOE order + current persistence + sequential breaker openings | PRIMARY CLEARING FAILURE / BACKUP CASCADE
System | Bus/incomer trip caused by downstream feeder breaker failure | Feeder protection + breaker failure + incomer/bus protection | Feeder protection trips first; incomer/bus-side protection trips later | Feeder trip command → feeder CB fails → BF/LBB → incomer/bus breaker trips | Feeder fault current continues until incomer/bus breaker opens | If feeder BF signal missing: time-order + feeder 52 status + current persistence + incomer trip | DOWNSTREAM FEEDER FAULT WITH LBB
System | Multiple-breaker cascade without bus fault | Feeder protection + backup/LBB + lockout | One primary fault declaration followed by backup trips | Primary breaker command → failed clearing → backup trips in defined hierarchy | Single fault signature persists while successive breakers open; no independent bus-fault signature | If topology/logic signals missing: reconstruct from SOE timestamps and current discontinuity after each breaker opening | CASCADE / BACKUP CLEARING — NOT AUTOMATICALLY A BUS FAULT
System | Successful backup clearing after primary breaker failure | Breaker failure + backup trip | Primary protection operates; local breaker fails; backup protection succeeds | Primary trip → BF interval → backup breaker(s) trip → fault current clears | Current persists during BF interval then collapses after backup breaker opening | If BF signal absent: current persistence + breaker sequence + final clearing location | BREAKER FAILURE WITH SUCCESSFUL BACKUP CLEARING
Instrumentation | VT failure / voltage measurement loss | VT supervision; voltage-dependent protection | VT supervision may alarm/block voltage-dependent elements | Voltage supervision change → protection block/alarm → no matching current fault | One/more voltage channels collapse while currents/power/system state do not support a real voltage fault | If VT supervision absent: phase-voltage comparison + sequence voltage + current/power continuity + independent voltage source | VT / MEASUREMENT ISSUE
Instrumentation | CT saturation / current measurement distortion | Differential; overcurrent; CT supervision | Protection may respond abnormally during high current | Protection operation occurs during high external/through-fault event | CT waveform clipping/distortion/asymmetry and current mismatch during high through-current | If CT flag absent: raw waveform + both-side current comparison + external-fault evidence | CT SATURATION SUSPECTED
Instrumentation | CT polarity/ratio/channel mismatch | Differential; metering; current supervision | Unexpected differential or imbalance may appear | Mismatch appears during otherwise balanced/known conditions | Current magnitude/phase relationship inconsistent between channels | If diagnostic unavailable: compare channels across healthy load and known faults; cross-check independent relay/meter records | CT CONFIGURATION / CHANNEL ISSUE
Control | Protection logic/control-system malfunction | Programmable logic; trip matrix; interlocking | Unexpected START/TRIP/lockout logic | SOE order contradicts expected protection sequence or command originates without valid initiating condition | DR may show no corresponding physical fault | If logic signals unavailable: compare relay events, breaker commands, SCADA commands and DR physical state | CONTROL / LOGIC MALOPERATION
Protection | Protection maloperation / unexplained trip | Any protection function | Protection declares trip | Trip sequence exists but independent evidence does not support fault | DR lacks corresponding physical signature or contradicts declared condition | Cross-check independent relay, neighboring device, CT/VT health, breaker status and topology | PROTECTION MALOPERATION SUSPECTED

## Protection Function Map
Function / ANSI Example | Generic Purpose | RCA Scenarios | Fallback if Function Signal Missing
21 / distance | Impedance-based fault location/zoning | Line phase/earth faults; external faults | V/I phasors → calculate impedance/R-X trajectory → topology
24 / V/Hz | Overexcitation/overfluxing | Transformer/generator overfluxing | Derive V/Hz from voltage waveform and frequency
25 / synch-check | Synchronism validation | Switching/closing events | Voltage magnitude/angle/frequency comparison + CB SOE
27 / undervoltage | Low voltage / voltage supervision | Faults; accidental energization; voltage events | DR RMS/sequence voltage
40 / underexcitation | Generator underexcitation | Loss of excitation | P/Q + phasor trajectory
46 / negative sequence | Phase unbalance / negative sequence | Motor/generator unbalance; phase loss | Calculate sequence components
48 / start supervision | Motor start-up supervision | Normal/prolonged start | CB close + current duration + speed
49 / thermal | Thermal overload | Motor/transformer thermal events | RMS current + temperature + duration
50/51 / phase OC | Phase overcurrent | Phase faults; external faults; motor events | Current waveform + voltage + topology
50G/N,51G/N,51N / earth fault | Earth fault detection | Earth faults | 3I0/residual current + voltage + topology
51LR / locked rotor | Motor locked rotor | Locked rotor | Persistent starting current + no acceleration
60 / VT supervision | Voltage measurement failure | VT failure / blocking | Cross-phase voltage consistency + current/power
62BF/50BF/51BF / breaker failure | Breaker failure / backup trip initiation | LBB, cascade clearing | Trip command + 52 status + current persistence + upstream trip
64 / earth fault | Machine/rotor/other earth fault depending application | Generator/motor/transformer earth conditions | Residual/neutral/third-harmonic evidence as applicable
67 / directional | Directional phase/earth fault | In-zone/out-of-zone feeder faults | V/I directional inference + topology
68 / inrush | Transformer inrush detection | Energization/inrush | CB close + asymmetric decaying waveform
78 / out-of-step | Power swing / pole slip | Generator/system out-of-step | Impedance/P-Q/angle trajectory
79 / autoreclose | Automatic reclosure | Temporary/persistent line faults | CB open/close sequence + repeated protection operation
81 / frequency | Frequency / df/dt | Frequency events; load shedding | Derive frequency from voltage waveform
85 / teleprotection | Remote transfer/tripping schemes | Line backup/remote trip events | Local/remote SOE correlation
86/94 / lockout/master trip | Trip distribution / lockout | Transformer/bus/breaker cascades | Trip matrix + breaker SOE
87 / differential | Internal-zone discrimination | Transformer/machine/line/bus faults | Multi-end current comparison + topology
HIZ/HIF / high impedance | High impedance fault detection | High impedance faults | Residual/sequence + waveform distortion
SOTF / switch-on-fault | Fault immediately after closing | Switch onto fault | CB close + immediate fault signature

## LBB Cascade Logic
Step | Question / Evidence | If YES | If NO / Fallback | RCA Meaning
1 | Was there a credible primary fault signature? | Identify fault type and probable location | Check protection/control/measurement issue before assuming fault | Primary fault determination
2 | Did primary protection START/OPERATE? | Record initiating protection | Use DR/SOE/neighbouring relay if signal missing | Primary detection
3 | Was a trip command issued to local breaker? | Record command timestamp | If no command, investigate blocking/logic/control | Primary clearing attempt
4 | Did local breaker status change correctly? | Confirm local breaker opened | Proceed to current persistence check | Breaker performance
5 | Did fault current disappear after local breaker opening? | Primary clearing successful | Persistent current → suspect breaker failure/LBB | Key LBB discriminator
6 | Did breaker-failure/LBB logic start or time out? | Record BF/LBB interval | Infer from elapsed time + persistent current + backup trip sequence | Breaker failure evidence
7 | Did upstream/incomer/bus-side breaker(s) trip afterward? | Identify backup clearing path | If not, investigate incomplete backup action | Cascade/backup action
8 | Did fault current disappear only after backup breaker(s) opened? | Strong LBB/cascade evidence | Look for alternate source/parallel feed | Physical validation
9 | Is there independent evidence of a bus fault? | Do not automatically label feeder LBB as bus fault; classify actual bus evidence separately | Classify as downstream feeder fault + LBB | Root-cause separation
10 | Final classification | Fault + breaker failure + backup clearing | If evidence incomplete, use PROBABLE/POSSIBLE | Avoid 'multiple breaker trip = bus fault' error

## Fallback Methodology
Evidence Level | Primary Evidence | Fallback Evidence | Rule
L1 - Relay | START/PICKUP, OPERATE, TRIP, stage, phase, direction, zone | Related protection function(s) and available status bits | Never infer a missing relay bit as if it existed.
L2 - SOE | Protection sequence, timers, trip commands, breaker status | Relay event timestamps + SCADA/SOE + neighboring relays | Reconstruct chronological causality from timestamps.
L3 - DR | Measured currents, voltages, sequence, impedance, P/Q, frequency, temperature, harmonics | Derive quantities mathematically from raw waveforms | Waveform-derived evidence may replace a missing dedicated indication.
Topology | Breaker positions, bus/feeder connectivity, source directions | Neighboring relay events and switching state | Location claims require topology context.
LBB | BF/LBB signal + timer | Trip command + unchanged breaker status + persistent current + delayed backup trip | Do not call a cascade a bus fault without independent bus-fault evidence.
Inrush | Dedicated inrush detector | CB close + asymmetric/distorted decaying current waveform | Harmonics support the diagnosis but are not mandatory.
In-zone | Configured distance/differential/REF zone | Impedance/current/voltage/topology inference | Label inferred zone decisions appropriately.
Confidence | Independent L1+L2+L3 agreement | Partial evidence with explicit missing channels | CONFIRMED / PROBABLE / POSSIBLE / NOT CONFIRMED.

## RCA Taxonomy
Classification | Meaning | Minimum Evidence
CONFIRMED | Independent evidence agrees across relay/SOE/DR or equivalent fallback paths | At least two independent evidence classes; preferably L1+L2+L3
PROBABLE | Strong physical and chronological evidence but one important signal/channel is missing | Strong DR/SOE or equivalent independent evidence
POSSIBLE | Plausible but insufficient to distinguish from alternatives | Partial evidence; alternatives remain
NOT CONFIRMED | Declared by relay/event but physical evidence does not support it | Contradictory or absent physical signature
BREAKER FAILURE / LBB | Primary fault exists but local breaker fails and backup clears | Persistent current after local trip + backup breaker clearing
CASCADE / BACKUP CLEARING | Multiple breakers operate as consequence of failed/backup clearing | Time-ordered sequential trip pattern
INSTRUMENTATION ISSUE | CT/VT/channel problem likely explains protection declaration | Measurement inconsistency/distortion
CONTROL / LOGIC ISSUE | Trip or blocking sequence inconsistent with physical fault | SOE/logic contradiction
PROTECTION MALOPERATION SUSPECTED | Protection operation lacks physical/system support after instrumentation/control checks | Relay declaration contradicted by independent evidence

## Scope & Notes
Topic | Note
Generalization | This matrix is vendor-neutral. ANSI numbers and function names are examples of protection concepts, not ABB-specific requirements.
Source basis | The uploaded ABB selection table was used as a reference for the protection-function terminology present in the original work; the decision logic is generalized beyond that vendor.
Settings | Pickup values, delays, distance zones, differential slopes, breaker clearing times and logic timers must come from the actual relay configuration/settings.
Waveforms | Raw DR waveform evidence is explicitly allowed as a fallback when a dedicated protection indication is absent.
Inrush | Do not require the dedicated inrush detector or harmonic channel to conclude inrush; use energization timing and waveform characteristics as fallback evidence.
LBB | Local breaker backup is treated separately from the initiating fault. Final RCA can therefore be 'feeder earth fault + feeder breaker failure + incomer backup clearing'.
Cascade | Multiple breaker trips do not automatically mean bus fault. Determine the initiating fault and the causal trip hierarchy first.